## Summary
Particulars | No. | Total MVAR | [14 empty] | Dharamjaygarh-Ranchi-II@Ranchi-240 SLR
765 240 MVAR BRs | 29 | 6960 |  |  | 765 kV S/S | 765 kV Lines | 765/400 kV ICTS | 765 kV Line Reactors in WR |  |  |  | 765 kV Bus Reactors in WR |  | Total Reactors & MVAR |  |  | Dharamjaygarh-Ranchi-I@Ranchi-240 SLR
765 330 MVAR BRs | 3 | 990 | [5 empty] | 240 MVAR |  | 330 MVAR |  | 240 MVAR | 330 MVAR |  |  |  | Gwalior-Jaipur-I@Jaipur 240
765 kV End-1 240 MVAR SLRs | 36 | 8640 | [5 empty] | S/W | Non S/W | S/W | Non S/W | [5 empty] | Gwalior-Jaipur-II@Jaipur 240
765 kV End-1 240 MVAR NSLRs | 15 | 3600 |  | No. | 29 | 79 | 62 | 54 | 40 | 12 | 8 | 29 | 3 | 146 |  |  | Solarpur-Raichur-I@Raichur240
765 kV End-1 330 MVAR SLRs | 8 | 2640 |  | MVAR | - | - | - | 12960 | 9600 | 3960 | 2640 | 6960 | 990 | 37110 |  |  | Solarpur-Raichur-II@Raichur240
765 kV End-1 330 MVAR NSLRs | 8 | 2640 | [14 empty] | Wardha-Nizamabad-I@Nizamabad-240
765 kV End-2 240 MVAR SLRs | 28 | 6720 |  |  | 1200 kV S/S | 1200 kV Lines | 1200/400 kV ICTS | [9 empty] | Wardha-Nizamabad-II@Nizamabad-240
765 kV End-2 240 MVAR NSLRs | 23 | 5520
765 kV End-2 330 MVAR SLRs | 4 | 1320
765 kV End-2 330 MVAR NSLRs | 0 | 0 |  | No. | 1 | 1 | 2
| 154 | 39030 |  | MVAR | - | - | -
Particulars | No. | Total MVAR |  |  | 400 kV S/S | 400 kV Lines | 400/220 & 400/132 kV ICTS | 400 kV Lines Reactors in WR | [5 empty] | 400 kV Bus Reactors in WR |  |  |  | Total
400 kV 50 MVAR BRs | 36 | 1800 | 50 |  |  |  |  | 50 MVAR |  | 63 MVAR |  | 80 MVAR |  | 50 MVAR | 63 MVAR | 80 MVAR | 125 MVAR
400 kV 63 MVAR BRs | 18 | 1134 | 63 |  |  |  |  | S/W | Non S/W | S/W | Non S/W | S/W | Non S/W
400 kV 80 MVAR BRs | 29 | 2320 | 80 | No. | 164 | 425 | 245 | 21 | 125 | 9 | 38 | 5 | 9 | 36 | 18 | 29 | 48 | 338
400 kV 125 MVAR BRs | 48 | 6000 | 125 | MVAR | - | - | - | 1050 | 6250 | 567 | 2394 | 400 | 720 | 1800 | 1134 | 2320 | 6000 | 22635
400 kV End-1 50 MVAR SLRs | 4 | 200 | 50
400 kV End-1 50 MVAR NSLRs | 64 | 3200 | 50
400 kV End-1 63 MVAR SLRs | 6 | 378 | 63 |  |  |  |  | Zerda-Binmal @Binmal 50 MVAR
400 kV End-1 63 MVAR NSLRs | 15 | 945 | 63 |  |  |  |  | Shujalpur-Rapp-1 @Rapp 50 MVAR
400 kV End-1 80 MVAR SLRs | 4 | 320 | 80 |  |  |  |  | Shujalpur-Rapp-2 @Rapp 50 MVAR
400 kV End-1 80 MVAR NSLRs | 5 | 400 | 80
400 kV End-2 50 MVAR SLRs | 11 | 550 | 50
400 kV End-2 50 MVAR NSLRs | 64 | 3200 | 50
400 kV End-2 63 MVAR SLRs | 4 | 252 | 63
400 kV End-2 63 MVAR NSLRs | 23 | 1449 | 63
400 kV End-2 80 MVAR SLRs | 3 | 240 | 80
400 kV End-2 80 MVAR NSLRs | 4 | 320 | 80
| 338 | 22708

## 400kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | Km | End-1 Owner | End-2 Owner | Conductor Type | SIL (Uncompensated) | No Load MVAR Generated | End1 LR |  | End2 LR | [6 empty] | End-1 | [5 empty] | End-2
[11 empty] | MVAR | S/W | MVAR | S/W | [5 empty] | 50 MVAR SLR | 50 MVAR NSLR | 63 MVAR SLR | 63 MVAR NSLR | 80 MVAR SLR | 80 MVAR NSLR | 50 MVAR SLR | 50 MVAR NSLR | 63 MVAR SLR | 63 MVAR NSLR | 80 MVAR SLR | 80 MVAR NSLR
1 | ACBIL | Bilaspur | 1 | ACBIL | 56 | ACBIL | WRTS-1 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - |  | X | B | Zpu | Z(ohms) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | ACBIL | MCCPL | 1 | ACBIL | 16 | ACBIL | MCCPL | Twin ACSR Moose | 517.1749 | 8.88 | - | - | - | - | Twin ACSR Moose | 0.0002075 | 0.00555 | 0.19336 | 309.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Akola | Aurangabad-PG | 1 | WRTS-1 | 178 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | 50 | - | Quad AAAC Moose | 0.0001676 | 0.00693 | 0.15551 | 248.8229 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
4 | Akola | Aurangabad-PG | 2 | WRTS-1 | 178 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | 50 | - | Quad ACSR Moose | 0.000158 | 0.00732 | 0.14692 | 235.0677 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
5 | Akola | Nandgaonpeth | 1 | MSETCL | 117 | MSETCL | Ratan India | Twin ACSR Moose | 517.1749 | 64.935 | - | - | - | - | Triple ACSR Snowbird | 0.0001718 | 0.00673 | 0.15977 | 255.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Akola | Akola(2) | 1 | MEGPTCL | 30 | MSETCL | MEGPTCL | Quad ACSR Moose | 680.6549 | 16.65 | - | - | - | - | Quad Bersimis | 0.000156 | 0.00746 | 0.14461 | 231.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Akola | Akola(2) | 2 | MEGPTCL | 30 | MSETCL | MEGPTCL | Quad ACSR Moose | 680.6549 | 16.65 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Akola(2) | Nandgaonpeth | 1 | APTCL | 104 | MEGPTCL | Ratan India | Twin ACSR Moose | 517.1749 | 57.72 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Akola(2) | Nandgaonpeth | 2 | APTCL | 104 | MEGPTCL | Ratan India | Twin ACSR Moose | 517.1749 | 57.72 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Alkud | Solapur-PG | 1 | WRTM | 12 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 6.66 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
11 | Amreli | Hadala | 1 | GETCO | 165 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 91.575 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Amreli | Chorania | 1 | GETCO | 164 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 91.02 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Amreli | Jetpur | 1 | GETCO | 96 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 53.28 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Amreli | Jetpur | 2 | GETCO | 66 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 36.63 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | APL-Mundra | Sami | 1 | ATIL | 282 | APL | ATIL | Twin ACSR Moose | 517.1749 | 156.51 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
16 | APL-Mundra | Sami | 2 | ATIL | 282 | APL | ATIL | Twin ACSR Moose | 517.1749 | 156.51 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
17 | APL-Mundra | Hadala | 1 | GETCO | 233 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 129.315 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
18 | APL-Mundra | Varsana | 1 | GETCO | 84 | APL | GETCO | Twin ACSR Moose | 517.1749 | 46.62 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | APL-Mundra | Varsana | 2 | GETCO | 84 | APL | GETCO | Twin ACSR Moose | 517.1749 | 46.62 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | APL-Mundra | Zerda(Kansari) | 1 | GETCO | 332 | APL | GETCO | Twin ACSR Moose | 517.1749 | 184.26 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
21 | Asoj | Chorania | 1 | GETCO | 177 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 98.235 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Asoj | Chorania | 2 | GETCO | 166 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 92.13 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Asoj | Kosamba | 1 | GETCO | 122 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 67.71 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Asoj | Wanakbori | 1 | GETCO | 76 | GETCO | GSECL | Twin ACSR Moose | 517.1749 | 42.18 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Athena | Raigarh-PS(Kotra) | 1 | ACPL | 25 | ACPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 18.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | Athena | Raigarh-PS(Kotra) | 2 | ACPL | 25 | ACPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 18.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | Aurangabad-M(Waluj) | Pune-PG(Shikrapur) | 1 | WRTM/ WRTS-I | 223 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 123.765 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | Aurangabad-M(Waluj) | Pune-PG(Shikrapur) | 2 | WRTM/ WRTS-I | 223 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 123.765 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Aurangabad-M(Waluj) | Aurangabad-PG | 1 | WRTS-1 | 54 | WRTS-1 | WRTS-1 | Quad ACSR Moose | 680.6549 | 39.528 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | Aurangabad-M(Waluj) | Aurangabad-PG | 2 | WRTS-1 | 54 | WRTS-1 | WRTS-1 | Quad ACSR Moose | 680.6549 | 39.528 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Aurangabad-M(Waluj) | Taptithanda | 1 | MSETCL | 135 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 74.925 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | Aurangabad-M(Waluj) | Deepnagar | 2 | MSETCL | 185 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 102.675 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | Aurangabad-PG | Boisar | 1 | WRTS-1 | 344 | WRTS-1 | WRTS-1 | Quad Zebra | 517.1749 | 181.485 | 80 | Yes | 80 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
34 | Aurangabad-PG | Boisar | 2 | WRTS-1 | 344 | WRTS-1 | WRTS-1 | Quad Zebra | 517.1749 | 181.485 | 80 | Yes | 80 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
35 | Bableshwar | Padghe | 1 | MSETCL | 174 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 96.57 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | Bableshwar | Padghe | 2 | MSETCL | 174 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 96.57 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | Bableshwar | Aurangabad-M(Waluj) | 1 | MSETCL | 131 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 72.705 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | Bableshwar | IB-Nasik | 1 | MSETCL | 72 | MSETCL | Ratan India | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | Bableshwar | IB-Nasik | 2 | MSETCL | 72 | MSETCL | Ratan India | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | Bachau | Ranchodpura | 1 | WRTS-2 | 282 | WRTS-2 | GETCO | Triple ACSR Snowbird | 625.887 | 189.786 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
41 | Bachau | Ranchodpura | 2 | WRTS-2 | 282 | WRTS-2 | GETCO | Triple ACSR Snowbird | 625.887 | 189.786 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
42 | Bachau | Varsana | 1 | WRTS-2 | 10 | WRTS-2 | GETCO | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | Bachau | Varsana | 2 | WRTS-2 | 10 | WRTS-2 | GETCO | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | Bachau | Chorania | 1 | WRTS-2 | 220 | WRTS-2 | GETCO | Triple ACSR Snowbird | 625.887 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | Bachau | Mansar | 1 | WRTS-2 | 128 | WRTS-2 | GETCO | Triple ACSR Snowbird | 625.887 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | Bhadrawati | Bhilai | 1 | WRTS-1 | 322 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 178.71 | 50 | - | 80 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
47 | Bhadrawati | Raipur | 1 | WRTS-1 | 333 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 184.815 | 50 | - | 80 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
48 | Bhadrawati | Raipur | 2 | WRTS-1 | 346 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 192.03 | 63 | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | Bhadrawati | Raipur | 3 | WRTS-1 | 346 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 192.03 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
50 | Bhadrawati | GWEL | 1 | GWEL | 28 | WRTS-1 | GWEL | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | Bhadrawati | GWEL | 2 | GWEL | 28 | WRTS-1 | GWEL | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | Bhadrawati | Parli-PG | 1 | WRTS-1 | 388 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 215.34 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
53 | Bhadrawati | Dhariwal | 1 | WRTS-1 | 15 | WRTS-1 | Dhariwal Infra | Twin ACSR Moose | 517.1749 | 8.325 | 63 | - | - | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | Bhadrawati HVDC | Ramagundam | 1 | SRTS-1 | 178 | WRTS-1 | SRTS-1 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | Bhadrawati HVDC | Ramagundam | 2 | SRTS-1 | 178 | WRTS-1 | SRTS-1 | Twin ACSR Moose | 517.1749 | 98.79 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | Bhilai | Raipur | 1 | WRTS-1 | 13 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 7.215 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | Bhilai | Seoni | 1 | WRTS-1 | 230 | CSPTCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 127.65 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | Bhilai | Bhatapara | 1 | WRTS-1 | 93 | CSPTCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 51.615 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
59 | Bhilai | Raita | 1 | CSPTCL | 56 | CSPTCL | CSPTCL | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | Bhilai | Raita | 2 | CSPTCL | 56 | CSPTCL | CSPTCL | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | Bhilai | Raita | 3 | CSPTCL | 56 | CSPTCL | CSPTCL | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | Bhopal-BDTCL | Bhopal-MP | 1 | BDTCL | 9 | BDTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 4.995 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | Bhopal-BDTCL | Bhopal-MP | 2 | BDTCL | 9 | BDTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 4.995 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | Bhopal-MP | Bina-MP | 1 | MPPTCL | 289 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 160.395 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
65 | Bhopal-MP | Bina-MP | 2 | MPPTCL | 273 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 151.515 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
66 | Bhopal-MP | Itarsi | 1 | MPPTCL | 98 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 54.39 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | Bhopal-MP | Itarsi | 2 | MPPTCL | 98 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 54.39 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | Bhopal-MP | Damoh | 1 | WRTS-2 | 214 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 118.77 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | Bhopal-MP | Damoh | 2 | WRTS-2 | 214 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 118.77 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | Bhusawal (Khadka) | Bableshwar | 1 | MSETCL | 220 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 122.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | Bhusawal (Khadka) | Aurangabad-M(Waluj) | 1 | MSETCL | 238 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 132.09 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
72 | Bhusawal (Khadka) | Akola | 1 | MSETCL | 182 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 101.01 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | Bhusawal (Khadka) | Deepnagar | 1 | MSETCL | 15 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | Bhusawal (Khadka) | Deepnagar | 2 | MSETCL | 15 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | Bina-MP | JP-Bina | 1 | MPPTCL | 20 | MPPTCL | Jaypee | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | Bina-MP | Bina-PG | 1 | WRTS-2 | 3 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | Bina-MP | Bina-PG | 2 | WRTS-2 | 3 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | Bina-MP | Bina-PG | 3 | WRTS-2 | 3 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | Bina-MP | Bina-PG | 4 | WRTS-2 | 3 | MPPTCL | WRST-2 | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | Bina-PG | Shujalpur | 1 | WRTS-2 | 200 | WRST-2 | WRST-2 | Twin ACSR Moose | 517.1749 | 111 | 63 | Yes | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
81 | Bina-PG | Shujalpur | 2 | WRTS-2 | 200 | WRST-2 | WRST-2 | Twin ACSR Moose | 517.1749 | 111 | 63 | Yes | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
82 | Bina-PG | JP-Bina | 1 | WRTS-2 | 20 | WRTS-2 | Jaypee | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | Bina-PG | Bina-NTS | 1 | WRTS-2 | 1 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 0.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | Bina-PG | NHPTL | 1 | WRTS-2 | 0.4 | WRTS-2 | NHPTL | Twin ACSR Moose | 517.1749 | 0.222 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | Birsingpur | Katni | 1 | MPPTCL | 118 | MPPGCL | MPPTCL | Twin ACSR Moose | 517.1749 | 65.49 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | Birsingpur | Katni | 2 | MPPTCL | 118 | MPPGCL | MPPTCL | Twin ACSR Moose | 517.1749 | 65.49 | 63 | - | - | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | CGPL | Jetpur | 1 | WRTS-2 | 334 | CGPL | GETCO | Triple ACSR Snowbird | 625.887 | 224.782 | 63 | Yes | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
88 | CGPL | Jetpur | 2 | WRTS-2 | 334 | CGPL | GETCO | Triple ACSR Snowbird | 625.887 | 224.782 | 63 | Yes | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
89 | CGPL | Bachau | 1 | WRTS-2 | 100 | CGPL | WRTS-2 | Triple ACSR Snowbird | 625.887 | 67.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | CGPL | Bachau | 2 | WRTS-2 | 100 | CGPL | WRTS-2 | Triple ACSR Snowbird | 625.887 | 67.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | CGPL | Bachau | 3 | WRTS-2 | 122 | CGPL | WRTS-2 | Triple ACSR Snowbird | 625.887 | 211.322 | 63 | Yes | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | CGPL | Bachau | 4 | WRTS-2 | 122 | CGPL | WRTS-2 | Triple ACSR Snowbird | 625.887 | 150.752 | 63 | Yes | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | Chakan | Pune-PG | 1 | MSETCL/ WRTM | 18 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | Champa | Lara | 1 | WRTS-1 | 112 | WRTS-1 | NTPC | Quad ACSR Moose | 681 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | Champa | Lara | 2 | WRTS-1 | 112 | WRTS-1 | NTPC | Quad ACSR Moose | 681 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | Chandrapur | Bhadrawati | 1 | WRTS-1 | 20 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | Chandrapur | Bhadrawati | 2 | WRTS-1 | 20 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | Chandrapur | Bhadrawati | 3 | WRTS-1 | 22 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | Chandrapur | Bhadrawati | 4 | WRTS-1 | 22 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | Chandrapur | Khaparkheda | 1 | MSETCL | 156 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 86.58 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | Chandrapur | Chandrapur-II | 1 | MSETCL | 1 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 0.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | Chandrapur | Chandrapur-II | 2 | MSETCL | 1 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 0.555 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | Chandrapur | Parli-M | 3 | MSETCL | 371 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 205.905 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
104 | Chandrapur-GCR | Chandrapur-II | 1 | MSETCL | 2 | MSETCL | MSETCL | Quad AAAC Moose | 643.0276 | 1.386 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | Chandrapur-GCR | Chandrapur-II | 2 | MSETCL | 2 | MSETCL | MSETCL | Quad AAAC Moose | 643.0276 | 1.386 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | Chandrapur-II | Dhariwal | 1 | MSETCL | 8 | MSETCL | Dhariwal Infra | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | Chandrapur-II | Dhariwal | 2 | MSETCL | 8 | MSETCL | Dhariwal Infra | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | Chandrapur-II | Nanded | 1 | MSETCL | 257 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 142.635 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | Chandrapur-II | Nanded | 2 | MSETCL | 276 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | Chhegaon | Julwania | 1 | MPPTCL | 114 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 63.27 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | Chorania | Kosamba | 1 | GETCO | 230 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 127.65 | 50 | - | 63 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
112 | Chorania | Kosamba | 2 | GETCO | 230 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 127.65 | 50 | - | 63 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
113 | Damoh | Birsingpur | 1 | WRTS-2 | 227 | WRTS-2 | MPPGCL | Twin ACSR Moose | 517.1749 | 125.985 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | Damoh | Birsingpur | 2 | WRTS-2 | 227 | WRTS-2 | MPPGCL | Twin ACSR Moose | 517.1749 | 125.985 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | Damoh | Katni | 1 | MPPTCL | 118 | WRTS-2 | MPPTCL | Twin ACSR Moose | 517.1749 | 65.49 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | DB-Power | Raigarh-PS(Kotra) | 1 | DB-Power | 18 | DB-Power | WRTS-1 | Quad ACSR Moose | 680.6549 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | DB-Power | Raigarh-PS(Kotra) | 2 | DB-Power | 18 | DB-Power | WRTS-1 | Quad ACSR Moose | 680.6549 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | Dehgam | Gandhar | 1 | WRTS-2 | 157 | WRTS-2 | NTPC | Twin ACSR Moose | 517.1749 | 87.135 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | Dehgam | Gandhar | 2 | WRTS-2 | 157 | WRTS-2 | NTPC | Twin ACSR Moose | 517.1749 | 87.135 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | Dehgam | Pirana-PG | 1 | WRTS-2 | 56 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | Dehgam | Sami | 1 | ATIL | 152 | WRTS-2 | ATIL | Twin ACSR Moose | 517.1749 | 84.36 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | Dehgam | Sami | 2 | ATIL | 152 | WRTS-2 | ATIL | Twin ACSR Moose | 517.1749 | 84.36 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | Dehgam | Ranchodpura | 1 | GETCO | 62 | WRTS-2 | GETCO | Twin ACSR Moose | 517.1749 | 34.41 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | Dehgam | Ranchodpura | 2 | GETCO | 62 | WRTS-2 | GETCO | Twin ACSR Moose | 517.1749 | 34.41 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | Dehgam | Wanakbori | 1 | WRTS-2 | 68 | WRTS-2 | GSECL | Twin ACSR Moose | 517.1749 | 37.74 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | Dehgam | Nicol-II | 1 | WRTS-2 | 25 | WRTS-2 | TPL | Twin ACSR Moose | 517.1749 | 31.08 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | Dharamjaygarh | Balco | 1 | BALCO | 23.2 | WRTS-1 | BALCO | Twin ACSR Moose | 517.1749 | 12.876 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | Dharamjaygarh | Balco | 2 | BALCO | 23.2 | WRTS-2 | BALCO | Twin ACSR Moose | 517.1749 | 12.876 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | Dhariwal | Parli-PG | 1 | WRTS-1 | 390 | Dhariwal Infra | WRTS-1 | Twin ACSR Moose | 517.1749 | 216.45 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
130 | Dhule-BDTCL | Dhule-MS | 1 | BDTCL | 18 | BDTCL | MSETCL | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | Dhule-BDTCL | Dhule-MS | 2 | BDTCL | 18 | BDTCL | MSETCL | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | Dhule-MS | Bableshwar | 1 | MSETCL | 170 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 94.35 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | Dhule-MS | Bableshwar | 2 | MSETCL | 170 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 94.35 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | Ektuni (Aurangabad(3)) | Bableshwar | 1 | MSETCL | 127 | MSETCL | MSETCL | Quad ACSR Moose | 680.6549 | 92.964 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | Ektuni (Aurangabad(3)) | Bableshwar | 2 | MSETCL | 127 | MSETCL | MSETCL | Quad ACSR Moose | 680.6549 | 92.964 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | Gandhar | Navsari | 1 | WRTS-2 | 106 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 58.83 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | Gandhar | Kosamba | 1 | WRTS-2 | 93 | NTPC | GETCO | Twin ACSR Moose | 517.1749 | 51.615 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | Gandhar | Hazira | 1 | EPTCL | 97 | NTPC | HAZIRA | Twin ACSR Moose | 517.1749 | 53.835 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | Gandhar | Hazira | 2 | EPTCL | 97 | NTPC | HAZIRA | Twin ACSR Moose | 517.1749 | 53.835 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | Gandhar | GPEC | 1 | GETCO | 13 | NTPC | GPEC | Twin ACSR Moose | 517.1749 | 7.215 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | Gandhar | Sugen | 1 | WRTS-2 | 67 | NTPC | TPL | Twin ACSR Moose | 517.1749 | 37.185 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | GPEC | Kasor | 1 | GPEC | 98 | GPEC | GETCO | Twin ACSR Moose | 517.1749 | 54.39 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | Hadala | Varsana | 1 | GETCO | 159 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 88.245 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | Hadala | Vadinar | 1 | GETCO | 113 | GETCO | ESSAR | Twin ACSR Moose | 517.1749 | 62.715 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | Hadala | Vadinar | 2 | GETCO | 113 | GETCO | ESSAR | Twin ACSR Moose | 517.1749 | 62.715 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | Hadala | Chorania | 1 | GETCO | 166 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 92.13 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | IEPL | Warora | 1 | MSETCL | 150 | IEPL | MSETCL | Twin ACSR Moose | 517.1749 | 83.25 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | IEPL | Koradi-II | 2 | MSETCL | 94 | IEPL | MSETCL | Twin ACSR Moose | 517.1749 | 52.17 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | Indira Sagar | Indore-MP | 1 | MPPTCL | 79 | MPPTCL | MPPTCL | Quad ACSR Moose | 680.6549 | 57.828 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | Indira Sagar | Indore-MP | 2 | MPPTCL | 80 | MPPTCL | MPPTCL | Quad ACSR Moose | 680.6549 | 58.56 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
151 | Indira Sagar | Nagda | 1 | MPPTCL | 188 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 104.34 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | Indore-MP | Indore-PG | 1 | WRTS-2 | 50 | MPPTCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 27.75 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | Indore-MP | Indore-PG | 2 | WRTS-2 | 50 | MPPTCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 27.75 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | Indore-MP | Nagda | 1 | MPPTCL | 108 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 59.94 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | Indore-MP | Asoj | 1 | WRTS-2 | 287 | MPPTCL | GETCO | Twin ACSR Moose | 517.1749 | 159.285 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
156 | Indore-MP | Asoj | 2 | WRTS-2 | 293 | MPPTCL | GETCO | Twin ACSR Moose | 517.1749 | 162.615 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
157 | Indore-PG | Pithampur | 1 | MPPTCL | 150 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 83.25 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | Indore-PG | Pithampur | 2 | MPPTCL | 150 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 83.25 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | Indore-PG | Khandwa | 1 | WRTS-2 | 169 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 |  | 80 | Yes | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | Indore-PG | Khandwa | 2 | WRTS-2 | 169 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 |  | 80 | Yes | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | Itarsi | Indore-MP | 1 | WRTS-2 | 207 | WRTS-2 | MPPTCL | Twin ACSR Moose | 517.1749 | 114.885 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
162 | Itarsi | Indore-MP | 2 | WRTS-2 | 214 | WRTS-2 | MPPTCL | Twin ACSR Moose | 517.1749 | 118.77 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
163 | Itarsi | Khandwa | 1 | WRTS-2 | 197 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 109.335 | 50 | Yes | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | Itarsi | Khandwa | 2 | WRTS-2 | 197 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 109.335 | 50 | Yes | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | Jabalpur | Itarsi | 1 | WRTS-2 | 232 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 128.76 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
166 | Jabalpur | Itarsi | 2 | WRTS-2 | 232 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 128.76 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
167 | Jabalpur | Itarsi | 3 | WRTS-2 | 234 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 129.87 | 50 | Yes | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
168 | Jabalpur | Itarsi | 4 | WRTS-2 | 234 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 129.87 | 50 | Yes | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
169 | Jabalpur | Sasan | 1 | WRTS-2 | 376 | WRTS-2 | SPL | Twin ACSR Moose | 517.1749 | 208.68 | 63 | - | 50 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
170 | Jabalpur | Jabalpur (PS) | 1 | WRTS-2 | 16 | WRTS-2 | WRTS-2 | Quad ACSR Moose | 680.6549 | 11.712 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | Jabalpur | Jabalpur (PS) | 2 | WRTS-2 | 16 | WRTS-2 | WRTS-2 | Quad ACSR Moose | 680.6549 | 11.712 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | Jabalpur (PS) | MB Power | 1 | WRTS-2 | 246 | WRTS-2 | MB-Power | Triple ACSR Snowbird | 625.887 | 165.558 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | Jabalpur (PS) | MB Power | 2 | WRTS-2 | 246 | WRTS-2 | MB-Power | Triple ACSR Snowbird | 625.887 | 165.558 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | Jabalpur (PS) | Jhabua Power | 1 | Jhabua Power Ltd | 65 | WRTS-2 | Jhabua Power | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Jabalpur (PS) | Jhabua Power | 2 | Jhabua Power Ltd | 65 | WRTS-2 | Jhabua Power | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Jaigad | New koyna | 1 | MSETCL | 55 | JAIGAD-IPP | MSETCL | Twin ACSR Moose | 517.1749 | 30.525 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | Jaigad | New koyna | 2 | MSETCL | 55 | JAIGAD-IPP | MSETCL | Twin ACSR Moose | 517.1749 | 30.525 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | Jejuri | Koyna stage-IV | 1 | MSETCL | 172 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 95.46 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | JPL | Raipur | 1 | JPL | 258 | JPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 143.19 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
180 | JPL | Raipur | 2 | JPL | 258 | JPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 143.19 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
181 | JPL | JPL_extn(Tamnar) | 1 | JPL | 2 | JPL | JPL | Quad ACSR Moose | 680.6549 | 1.11 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | JPL_extn(Tamnar) | Tamnar-PS | 1 | JPL | 10 | JPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | JPL_extn(Tamnar) | Tamnar-PS | 2 | JPL | 10 | JPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | JPL_extn(Tamnar) | Tamnar-PS | 4 | JPL | 10 | JPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | JPL_extn(Tamnar) | Tamnar-PS | 3 | JPL | 10 | JPL | WRTS-1 | Quad ACSR Moose | 680.6549 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | Kala | Vapi | 1 | WRTS-2 | 49 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 27.195 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | Kala | Vapi | 2 | WRTS-2 | 52 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 28.86 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | Kala | Boisar | 1 | WRTS-2 | 61 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 33.855 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | Kalwa | Padghe | 1 | MSETCL | 72 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | Kalwa | Padghe | 2 | MSETCL | 72 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | Kalwa | Kharghar | 1 | MSETCL | 28 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | Kalwa | Pune-PG | 1 | MSETCL/ WRTM | 104 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 57.72 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | Karad | Kolhapur | 1 | MSETCL | 105 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | Karad | Kolhapur | 2 | MSETCL | 105 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | Karad | Jaigad | 1 | MSETCL | 111 | MSETCL | JAIGAD-IPP | Twin ACSR Moose | 517.1749 | 61.605 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | Karad | Jaigad | 2 | MSETCL | 111 | MSETCL | JAIGAD-IPP | Twin ACSR Moose | 517.1749 | 61.605 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | Karad | New Koyna | 1 | MSETCL | 72 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | Karad | New Koyna | 2 | MSETCL | 72 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 39.96 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | Karad | Lonikhand | 1 | MSETCL | 161 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 89.355 | 80 | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
200 | Kasor | Chorania | 1 | GETCO | 103 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 57.165 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | Khandwa | Dhule-MS | 1 | WRTS-2 | 262 | WRTS-2 | MSETCL | Twin ACSR Moose | 517.1749 | 145.41 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
202 | Khandwa | Dhule-MS | 2 | WRTS-2 | 262 | WRTS-2 | MSETCL | Twin ACSR Moose | 517.1749 | 145.41 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
203 | Khandwa | Rajgarh | 1 | WRTS-2 | 221 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 122.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | Khandwa | Rajgarh | 2 | WRTS-2 | 221 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 122.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | Khandwa | Betul | 1 | WRTS-2 | 169 | WRTS-2 | WRTS-2 | Quad ACSR Moose | 680.6549 | 123.708 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | Khandwa | Betul | 2 | WRTS-2 | 169 | WRTS-2 | WRTS-2 | Quad ACSR Moose | 680.6549 | 123.708 | 50 | - | 50 | Yes | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | Kharghar | Pune-PG | 1 | MSETCL/ WRTM | 96 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 47.175 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | Kolhapur | Kolhapur-PG | 1 | WRTS-1 | 39 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 21.645 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | Kolhapur | Kolhapur-PG | 2 | WRTS-1 | 39 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 21.645 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | Kolhapur | Alkud | 1 | MSETCL/ WRTM | 12 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 6.66 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | Kolhapur | Solapur-PG | 2 | WRTM | 220 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 122.1 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
212 | Kolhapur-PG | Mapusa | 1 | WRTS-1 | 156 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 86.58 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | Kolhapur-PG | Mapusa | 2 | WRTS-1 | 156 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 86.58 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | Koradi | Bhusawal (Khadka) | 2 | MSETCL | 343 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 190.365 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
215 | Koradi | Satpura | 1 | WRTS-1 | 149 | WRTS-1 | WRTS-2 | Twin ACSR Moose | 517.1749 | 82.695 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
216 | Koradi | Bhilai | 1 | WRTS-1 | 272 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
217 | Koradi | Khaparkheda | 1 | MSETCL | 10 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | Koradi | Khaparkheda | 2 | MSETCL | 10 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 5.55 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | Koradi-II | Koradi-III | 1 | MSETCL | 38 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 21.09 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | Koradi-II | Koradi-III | 2 | MSETCL | 39 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 21.645 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | Korba (W) | Korba-NTPC | 1 | WRTS-1 | 14 | CSPGCL | NTPC | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | Korba (W) | Raita | 1 | CSPTCL | 144 | CSPGCL | CSPTCL | Twin ACSR Moose | 517.1749 | 79.92 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | Korba (W) | Korba (W)-Ext | 1 | CSPTCL | 1 | CSPGCL | CSPTCL | Twin ACSR Moose | 517.1749 | 0.555 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | Korba (W)-Ext | Bhilai | 1 | CSPTCL | 220 | CSPGCL | CSPTCL | Twin ACSR Moose | 517.1749 | 122.1 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
225 | Korba (W)-Ext | Marwa | 1 | CSPTCL | 60 | CSPGCL | CSPTCL | Twin ACSR Moose | 517.1749 | 33.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | Korba-NTPC | Bhilai | 1 | WRTS-1 | 197 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 109.335 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
227 | Korba-NTPC | Bhilai | 2 | WRTS-1 | 192 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 106.56 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
228 | Korba-NTPC | Raipur | 1 | WRTS-1 | 212 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 117.66 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
229 | Korba-NTPC | Raipur | 2 | WRTS-1 | 212 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 117.66 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
230 | Korba-NTPC | Sipat | 1 | WRTS-1 | 68 | NTPC | NTPC | Twin ACSR Moose | 517.1749 | 37.74 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | Korba-NTPC | Essar_Mahan | 1 | WRTS-1 | 218 | NTPC | Mahan | Twin ACSR Moose | 517.1749 | 120.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | Korba-NTPC | Vindhyachal | 2 | WRTS-1 | 289 | WRTS-1 | WRTS-2 | Twin ACSR Moose | 517.1749 | 160.395 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
233 | Korba-NTPC | Bhatapara | 1 | WRTS-1 | 124 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 68.82 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | Korba-NTPC | Birsingpur | 2 | WRTS-1 | 226 | NTPC | MPPGCL | Twin ACSR Moose | 517.1749 | 125.43 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
235 | Korba-NTPC | Birsingpur | 1 | WRTS-1 | 226 | NTPC | MPPGCL | Twin ACSR Moose | 517.1749 | 125.43 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
236 | Koyna stage-IV | Lonikhand | 1 | MSETCL | 183 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 101.565 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | Koyna stage-IV | New Koyna | 1 | MSETCL | 14 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | Koyna stage-IV | New Koyna | 2 | MSETCL | 14 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | KSK Mahanadi | Champa | 3 | WRTS-1 | 27 | KSK | WRTS-1 | Quad ACSR Moose | 680.6549 | 19.764 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | KSK Mahanadi | Champa | 4 | WRTS-1 | 27 | KSK | WRTS-1 | Quad ACSR Moose | 680.6549 | 19.764 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | KWPCL | Raigarh-PS(Kotra) | 1 | KWPCL | 19 | KWPCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 10.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | KWPCL | Raigarh-PS(Kotra) | 2 | KWPCL | 19 | KWPCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 10.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | Lara | Raigarh-PS(Kotra) | 1 | WRTS-1 | 18 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | Lara | Raigarh-PS(Kotra) | 2 | WRTS-1 | 18 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 9.99 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | Lonikhand | Jejuri | 1 | MSETCL | 48 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 26.64 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | Lonikhand | Chakan | 1 | MSETCL | 37 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 20.535 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | Lonikhand | Pune-PG | 1 | MSETCL/ WRTM | 40 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 22.2 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | Lonikhand-II | Lonikhand | 1 | MSETCL | 1 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 0.555 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | Lonikhand-II | Lonikhand | 2 | MSETCL | 1 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 0.555 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | Magarawada | Kala | 1 | WRTS-2 | 53 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 29.415 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | Magarawada | Boisar | 1 | WRTS-2 | 97 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 53.835 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | Magarawada | Navsari | 1 | WRTS-2 | 126 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 69.93 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | Magarawada | Navsari | 2 | WRTS-2 | 126 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 69.93 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | Malwa | Chhegaon | 1 | MPPTCL | 53 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 29.415 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | Malwa | Pithampur | 1 | MPPTCL | 136 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | Malwa | Pithampur | 2 | MPPTCL | 136 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | Malwa | Julwania | 1 | MPPTCL | 170 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 94.35 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | Mansar | Chorania | 1 | WRTS-2 | 94 | GETCO | GETCO | Triple ACSR Snowbird | 625.887 | 63.262 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
259 | MCCPL | Bilaspur | 1 | WRTS-1 | 45 | MCCPL | WRTS-1 | Twin ACSR Moose | 517.1749 | 24.975 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | Mouda* | Betul* | 1 | WRTS-2 | 86 | NTPC | WRTS-2 | Quad ACSR Moose | 680.6549 | 62.952 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | Mouda* | Betul* | 2 | WRTS-2 | 86 | NTPC | WRTS-2 | Quad ACSR Moose | 680.6549 | 62.952 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | Nagda | Dehgam | 1 | WRTS-2 | 331 | MPPTCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 183.705 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
263 | Nagda | Dehgam | 2 | WRTS-2 | 331 | MPPTCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 183.705 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
264 | Nagda | Shujalpur | 1 | WRTS-2 | 151 | MPPTCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 83.805 | - | - | 63 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | Nagda | Shujalpur | 2 | WRTS-2 | 151 | MPPTCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 83.805 | - | - | 63 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | Nandgaonpeth | Koradi | 1 | MSETCL | 140 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 77.7 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | Navsari | DGEN | 1 | TPL | 105 | WRTS-2 | DGEN | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | Navsari | DGEN | 2 | TPL | 105 | WRTS-2 | DGEN | Twin ACSR Moose | 517.1749 | 58.275 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | Navsari | Kakrapar-3&4 | 1 | WRTS-2 | 38 | WRTS-2 | NPCIL | Twin ACSR Moose | 517.1749 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | Navsari | Kakrapar-3&4 | 2 | WRTS-2 | 38 | WRTS-2 | NPCIL | Twin ACSR Moose | 517 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | NSPCL | Raipur | 1 | NSPCL | 14 | NSPCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | NSPCL | Raipur | 2 | NSPCL | 14 | NSPCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 7.77 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | Padghe | Boisar | 1 | WRTS-2 | 101 | MSETCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 56.055 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | Padghe | Nagothane | 1 | MSETCL | 116 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 64.38 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | Padghe | Nagothane | 2 | MSETCL | 116 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 64.38 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | Parli-M | Lonikhand-II | 1 | MSETCL | 284 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 157.62 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
277 | Parli-M | Lonikhand-II | 2 | MSETCL | 284 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 157.62 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
278 | Parli-M | Sholapur-M | 1 | MSETCL | 182 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 101.01 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | Parli-M | Nanded | 1 | MSETCL | 163 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 90.465 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | Parli-M | Nanded | 2 | MSETCL | 160 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 |  | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | Parli-M | Parli-PG | 1 | WRTS-1 | 5 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 2.775 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | Parli-M | Parli-PG | 2 | WRTS-1 | 5 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 2.775 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | Parli-PG | Pune-PG(Shikrapur) | 1 | WRTM/ WRTS-1 | 272 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
284 | Parli-PG | Pune-PG(Shikrapur) | 2 | WRTM/ WRTS-1 | 272 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
285 | Parli-PG | Solapur-PG | 1 | WRTM | 65 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | Parli-PG | Solapur-PG | 2 | WRTM | 65 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | Pathadi | Bilaspur | 1 | LANCO | 31 | LANCO | WRTS-1 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | Pathadi | Bilaspur | 2 | LANCO | 31 | LANCO | WRTS-1 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | Pirana-PG | Nicol-II | 1 | WRTS-2 | 45 | WRTS-2 | TPL | Twin ACSR Moose | 517.1749 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | Pirana-T | Pirana-PG | 1 | TPL | 6 | TPL | WRTS-2 | Twin ACSR Moose | 517.1749 | 3.33 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | Pirana-T | Pirana-PG | 2 | TPL | 6 | TPL | WRTS-2 | Twin ACSR Moose | 517.1749 | 3.33 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | Pune-PG(Shikrapur) | Pune-PG | 1 | WRTM/ WRTS-1 | 64 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | Pune-PG(Shikrapur) | Pune-PG | 2 | WRTM/ WRTS-1 | 64 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | Pune-PG(Shikrapur) | Pune-PG | 3 | WRTM/ WRTS-1 | 64 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | Pune-PG(Shikrapur) | Pune-PG | 4 | WRTM/ WRTS-1 | 64 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 35.52 | - | - | 50 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | Raigarh | Jharsuguda | 1 | WRTS-1/ ERTS-2 | 110 | WRTS-1 | ERTS-2 | Twin ACSR Moose | 517.1749 | 61.05 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | Raigarh | Jharsuguda | 2 | WRTS-1/ ERTS-2 | 110 | WRTS-1 | ERTS-2 | Twin ACSR Moose | 517.1749 | 61.05 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | Raigarh | Rourkela | 1 | WRTS-1/ ERTS-2 | 230 | WRTS-1 | ERTS-2 | Twin ACSR Moose | 517.1749 | 127.65 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | Raigarh | Rourkela | 2 | WRTS-1/ ERTS-2 | 230 | WRTS-1 | ERTS-2 | Twin ACSR Moose | 517.1749 | 73.815 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | Raigarh | Raipur | 1 | WRTS-1 | 217 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 120.435 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
301 | Raigarh | Raipur | 2 | WRTS-1 | 217 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 120.435 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
302 | Raigarh | Raigarh-PS(Kotra) | 1 | WRTS-1 | 7 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 3.885 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | Raigarh | Raigarh-PS(Kotra) | 2 | WRTS-1 | 7 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 3.885 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | Raigarh | Raipur | 3 | WRTS-1 | 221 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 122.655 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
305 | Raigarh | Raipur | 4 | WRTS-1 | 221 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 122.655 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
306 | Raipur | Wardha | 1 | WRTS-1 | 371 | WRTS-1 | WRTS-1 | Quad ACSR Moose | 680.6549 | 271.572 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
307 | Raipur | Wardha | 2 | WRTS-1 | 371 | WRTS-1 | WRTS-1 | Quad ACSR Moose | 680.6549 | 271.572 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
308 | Raipur | Raipur-PS(Durg) | 1 | WRTS-1 | 22 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | Raipur | Raipur-PS(Durg) | 2 | WRTS-1 | 22 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 12.21 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | Raipur-PS(Durg) | GMR-CG | 1 | GMR | 65 | WRTS-1 | GMR-CG | Quad ACSR Moose | 681 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | Raipur-PS(Durg) | GMR-CG | 2 | GMR | 65 | WRTS-1 | GMR-CG | Quad ACSR Moose | 681 | 36.075 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | Raita | Marwa | 1 | CSPTCL | 141 | CSPTCL | CSPTCL | Quad AAAC Moose | 643.0276 | 78.255 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | Raita | Marwa | 2 | CSPTCL | 141 | CSPTCL | CSPTCL | Quad AAAC Moose | 643.0276 | 78.255 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | Raita | Jagdalpur | 2 | CSPTCL | 328 | CSPGCL | CSPTCL | Twin ACSR Moose | 517 |  | - | - | 80 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | Rajgarh | Nagda | 1 | WRTS-2 | 104 | WRTS-2 | MPPTCL | Twin ACSR Moose | 517.1749 | 57.72 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
316 | Rajgarh | Nagda | 2 | WRTS-2 | 104 | WRTS-2 | MPPTCL | Twin ACSR Moose | 517.1749 | 57.72 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
317 | Rajgarh | Kasor | 1 | WRTGPL | 243 | WRTS-2 | GETCO | Twin ACSR Moose | 517.1749 | 134.865 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
318 | Rajgarh | Kasor | 2 | WRTGPL | 243 | WRTS-2 | GETCO | Twin ACSR Moose | 517.1749 | 134.865 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
319 | Ranchodpura | Zerda(Kansari) | 1 | WRTGPL | 140 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 77.7 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | Ranchodpura | Zerda(Kansari) | 2 | WRTGPL | 140 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 77.7 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | Ranchodpura | Chorania | 1 | WRTGPL | 103 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 57.165 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | Ranchodpura | Chorania | 2 | WRTGPL | 103 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 57.165 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | RGPPL | New Koyna | 1 | MSETCL | 60 | RGPPL | MSETCL | Twin ACSR Moose | 517.1749 | 33.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | RGPPL | New Koyna | 2 | MSETCL | 60 | RGPPL | MSETCL | Twin ACSR Moose | 517.1749 | 33.3 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | RGPPL | Nagothane | 1 | MSETCL | 136 | RGPPL | MSETCL | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | RGPPL | Nagothane | 2 | MSETCL | 136 | RGPPL | MSETCL | Twin ACSR Moose | 517.1749 | 75.48 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | RKM | Raigarh-PS(Kotra) | 1 | RKM | 27 | RKM | WRTS-1 | Quad ACSR Moose | 680.6549 | 19.764 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | RKM | Raigarh-PS(Kotra) | 2 | RKM | 27 | RKM | WRTS-1 | Quad ACSR Moose | 680.6549 | 19.764 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | Satna | Bina-PG | 1 | WRTS-2 | 276 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 153.18 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
330 | Satna | Bina-PG | 2 | WRTS-2 | 276 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 153.18 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
331 | Satna | Bina-NTS | 3 | WRTS-2 | 272 | WRTS-2 | NHPTL | Twin ACSR Moose | 517.1749 | 150.96 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | Satna | Bina-PG | 4 | WRTS-2 | 273 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 151.515 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
333 | Satna | JP-Nigrie | 1 | Jaypee | 161 | WRTS-2 | Jaypee | Quad ACSR Moose | 680.6549 | 117.852 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | Satna | JP-Nigrie | 2 | Jaypee | 161 | WRTS-2 | Jaypee | Quad ACSR Moose | 680.6549 | 117.852 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | Satpura | Indira sagar | 1 | MPPTCL | 189 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 104.895 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | Satpura | Itarsi | 1 | WRTS-2 | 79 | MPPTCL | WRTS-2 | Twin ACSR Moose | 517.1749 | 43.845 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | Satpura | Astha | 1 | MPPTCL | 240 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 133.2 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | Satpura | Astha | 2 | MPPTCL | 240 | MPPTCL | MPPTCL | Twin ACSR Moose | 517.1749 | 133.2 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | Seoni | Satpura | 1 | WRTS-1 | 156 | WRTS-1 | MPPTCL | Twin ACSR Moose | 517.1749 | 86.58 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | Seoni | Khandwa | 1 | WRTS-1 | 352 | WRTS-1 | WRTS-2 | Quad AAAC Moose | 643.0276 | 243.936 | 80 | - | 80 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
341 | Seoni | Khandwa | 2 | WRTS-1 | 352 | WRTS-1 | WRTS-2 | Quad AAAC Moose | 643.0276 | 243.936 | 80 | - | 80 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
342 | Sholapur-M | Solapur-PG | 1 | MSETCL | 178 | MSETCL | WRTS-1 | Twin ACSR Moose | 517.1749 | 98.79 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | Shujalpur | RAPP | 1 | RTCL | 201 | WRTS-2 | NPCIL | Twin ACSR Moose | 517.1749 | 111.555 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
344 | Shujalpur | RAPP | 2 | RTCL | 201 | WRTS-2 | NPCIL | Twin ACSR Moose | 517.1749 | 111.555 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
345 | Sipat | Raipur | 1 | WRTS-1 | 149 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 82.695 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | Sipat | Raipur | 2 | WRTS-1 | 149 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 82.695 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | Sipat | Raipur | 3 | WRTS-1 | 156 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 86.58 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | Sipat | Ranchi | 1 | WRTS-1/ERTS-1 | 405 | NTPC | ERTS-1 | Twin ACSR Moose | 517.1749 | 224.775 | 80 | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
349 | Sipat | Ranchi | 2 | WRTS-1/ERTS-1 | 405 | NTPC | ERTS-1 | Twin ACSR Moose | 517.1749 | 224.775 | 80 | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
350 | SKS | Raigarh-PS(Kotra) | 1 | WRTS-1 | 28 | SKS | WRTS-1 | Quad ACSR Moose | 680.6549 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | SKS | Raigarh-PS(Kotra) | 2 | WRTS-1 | 28 | SKS | WRTS-1 | Quad ACSR Moose | 680.6549 | 15.54 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | Soja | Wanakbori | 1 | GETCO | 95 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 52.725 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | Soja | Dehgam | 1 | WRTS-2 | 41 | GETCO | WRTS-2 | Twin ACSR Moose | 517.1749 | 22.755 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | Soja | Zerda(Kansari) | 1 | GETCO | 135 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 74.925 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | Solapur-PG | Solapur-NTPC | 1 | WRTS-1 | 11 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 6.105 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | Solapur-PG | Solapur-NTPC | 2 | WRTS-1 | 11 | NTPC | WRTS-1 | Twin ACSR Moose | 517.1749 | 6.105 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | Solapur-PG | Solapur-NTPC | 3 | WRTS-1 | 12 | NTPC | WRTS-1 | Quad ACSR Moose | 680.6549 | 6.105 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | Solapur-PG | Solapur-NTPC | 4 | WRTS-1 | 12 | NTPC | WRTS-1 | Quad ACSR Moose | 680.6549 | 6.105 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | SSP | Dhule-MS | 1 | MSETCL | 236 | SSNNL | MSETCL | Twin ACSR Moose | 517.1749 | 130.98 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
360 | SSP | Dhule-MS | 2 | MSETCL | 236 | SSNNL | MSETCL | Twin ACSR Moose | 517.1749 | 130.98 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
361 | SSP | Asoj | 1 | GETCO | 83 | SSNNL | GETCO | Twin ACSR Moose | 517.1749 | 46.065 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | SSP | Rajgarh | 1 | MPPTCL | 178 | SSNNL | WRTS-2 | Twin ACSR Moose | 517.1749 | 98.79 | - | - | 63 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | SSP | Rajgarh | 2 | MPPTCL | 178 | SSNNL | WRTS-2 | Twin ACSR Moose | 517.1749 | 98.79 | - | - | 63 | Yes | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | SSP | Kasor | 1 | GETCO | 146 | SSNNL | GETCO | Twin ACSR Moose | 517.1749 | 81.03 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | Sugen | Uno-Sugen | 1 | TPL | 3 | TPL | TPL | Twin ACSR Moose | 517.1749 | 1.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | Sugen | Pirana-T | 1 | TPL | 212 | TPL | TPL | Twin ACSR Moose | 517.1749 | 117.66 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
367 | Taptithanda | Deepnagar | 1 | MSETCL | 203 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 112.665 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | Taptithanda | Ektuni (Aurangabad(3)) | 1 | MSETCL | 5 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 2.775 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | Taptithanda | Ektuni (Aurangabad(3)) | 2 | MSETCL | 5 | MSETCL | MSETCL | Twin ACSR Moose | 517.1749 | 2.775 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | Tarapur-3&4 | Padghe | 1 | WRTS-1 | 91 | NPCIL | MSETCL | Twin ACSR Moose | 517.1749 | 50.505 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | Tarapur-3&4 | Padghe | 2 | WRTS-1 | 91 | NPCIL | MSETCL | Twin ACSR Moose | 517.1749 | 50.505 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | Tarapur-3&4 | Boisar | 1 | WRTS-2 | 21 | NPCIL | WRTS-2 | Twin ACSR Moose | 517.1749 | 11.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | Tarapur-3&4 | Boisar | 2 | WRTS-2 | 21 | NPCIL | WRTS-2 | Twin ACSR Moose | 517.1749 | 11.655 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | Tiroda | Warora | 1 | MEGPTCL | 219 | APML | MEGPTCL | Twin ACSR Moose | 517.1749 | 121.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | Tiroda | Warora | 2 | MEGPTCL | 219 | APML | MEGPTCL | Twin ACSR Moose | 517.1749 | 121.545 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
376 | TRN | Tamnar-PS | 1 | WRTS-1 | 15 | TRN | WRTS-1 | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
377 | TRN | Tamnar-PS | 2 | WRTS-1 | 15 | TRN | WRTS-1 | Twin ACSR Moose | 517.1749 | 8.325 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | Ukai | Kosamba | 1 | GETCO | 81 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 44.955 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Ukai | Kosamba | 2 | GETCO | 68 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 37.74 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | Ukai | Navsari | 1 | GETCO | 83 | GETCO | WRTS-2 | Twin ACSR Moose | 517.1749 | 46.065 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381 | Uno-Sugen | Pirana-T | 1 | TPL | 209 | TPL | TPL | Twin ACSR Moose | 517.1749 | 115.995 | - | - | 50 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
382 | Vadinar | Bachau | 1 | WRTS-2 | 226 | ESSAR | WRTS-2 | Twin ACSR Moose | 517.1749 | 125.43 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
383 | Vadinar | Bachau | 2 | WRTS-2 | 226 | ESSAR | WRTS-2 | Twin ACSR Moose | 517.1749 | 125.43 | - | - | 63 | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
384 | Vadodara-PS | Pirana-PG | 1 | WRTS-2 | 131 | WRTS-2 | WRTS-2 | Quad ACSR Moose | 680.6549 | 95.892 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385 | Vadodara-PS | Pirana-PG | 2 | WRTS-2 | 131 | WRTS-2 | WRTS-2 | Quad ACSR Moose | 680.6549 | 95.892 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
386 | Vadodara-PS | Asoj | 1 | WRTS-2 | 14 | WRTS-2 | GETCO | Quad ACSR Moose | 680.6549 | 10.248 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387 | Vadodara-PS | Asoj | 2 | WRTS-2 | 14 | WRTS-2 | GETCO | Quad ACSR Moose | 680.6549 | 10.248 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388 | Vapi | Boisar | 1 | WRTS-2 | 91 | WRTS-2 | WRTS-2 | Twin ACSR Moose | 517.1749 | 50.505 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
389 | Vapi | Sugen | 1 | WRTS-2 | 118 | WRTS-2 | TPL | Twin ACSR Moose | 517.1749 | 65.49 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
390 | Vapi | Kakrapar-3&4 | 1 | WRTS-2 | 117 | WRTS-2 | NPCIL | Twin ACSR Moose | 517 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
391 | Vapi | Kakrapar-3&4 | 2 | WRTS-2 | 117 | WRTS-2 | NPCIL | Twin ACSR Moose | 517 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
392 | Veloda | Charnaka | 1 | GETCO | 199 | GETCO | GETCO | Twin ACSR Moose | 517.1749 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
393 | Veloda | Charnaka | 2 | GETCO | 199 | GETCO | GETCO | Twin ACSR Moose | 517.1749 |  | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
394 | Vindhyachal | Jabalpur | 1 | WRTS-2 | 360 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 199.8 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
395 | Vindhyachal | Jabalpur | 2 | WRTS-2 | 360 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 199.8 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
396 | Vindhyachal | Jabalpur | 4 | WRTS-2 | 389 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 215.895 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
397 | Vindhyachal | Satna | 1 | WRTS-2 | 267 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 148.185 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
398 | Vindhyachal | Satna | 2 | WRTS-2 | 267 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 148.185 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
399 | Vindhyachal | Satna | 3 | WRTS-2 | 258 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 143.19 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
400 | Vindhyachal | Satna | 4 | WRTS-2 | 258 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 143.19 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
401 | Vindhyachal | Sasan | 3 | WRTS-2 | 20 | NTPC | SPL | Twin ACSR Moose | 517.1749 | 11.1 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
402 | Vindhyachal | Essar_Mahan | 1 | WRTS-2 | 41 | NTPC | Mahan | Twin ACSR Moose | 517.1749 | 22.755 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
403 | Vindhyachal-III | Vindhyachal-V | 1 | NTPC | 4 | NTPC | NTPC | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
404 | Vindhyachal-III | Vindhyachal-V | 2 | NTPC | 4 | NTPC | NTPC | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
405 | Vindhyachal-IV | Vindhyachal-V | 1 | NTPC | 4 | NTPC | NTPC | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
406 | Vindhyachal-IV | Vindhyachal-V | 2 | NTPC | 4 | NTPC | NTPC | Quad ACSR Moose | 680.6549 | 2.928 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
407 | Vindhyachal-IV | Vindhyachal-PS | 1 | WRTS-2 | 31 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
408 | Vindhyachal-IV | Vindhyachal-PS | 2 | WRTS-2 | 31 | NTPC | WRTS-2 | Twin ACSR Moose | 517.1749 | 17.205 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
409 | Vindhyachal-PS | Sasan | 1 | WRTS-2 | 8 | NTPC | SPL | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
410 | Vindhyachal-PS | Sasan | 2 | WRTS-2 | 8 | WRTS-2 | SPL | Twin ACSR Moose | 517.1749 | 4.44 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
411 | Vindhyachal-PS | Rihand | 1 | WRTS-2/NRTS-1 | 35 | WRTS-2 | NRTS-1 | Quad Bersimis | 691.5238 | 26.11 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
412 | Vindhyachal-PS | Rihand | 2 | WRTS-2/NRTS-1 | 28 | WRTS-2 | NRTS-1 | Quad Bersimis | 691.5238 | 20.888 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
413 | Wardha | Parli-PG | 1 | WRTS-1 | 337 | WRTS-1 | WRTS-1 | Quad ACSR Moose | 680.6549 | 246.684 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
414 | Wardha | Parli-PG | 2 | WRTS-1 | 337 | WRTS-1 | WRTS-1 | Quad ACSR Moose | 680.6549 | 246.684 | 63 | - | 63 | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
415 | Wardha | Akola | 1 | WRTS-1 | 162 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 89.91 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
416 | Wardha | Akola | 2 | WRTS-1 | 162 | WRTS-1 | WRTS-1 | Twin ACSR Moose | 517.1749 | 89.91 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
417 | Wardha | Mouda | 1 | WRTS-1 | 124 | WRTS-1 | NTPC | Quad ACSR Moose | 680.6549 | 90.768 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
418 | Wardha | Mouda | 2 | WRTS-1 | 124 | WRTS-1 | NTPC | Quad ACSR Moose | 680.6549 | 90.768 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
419 | Wardha | Warora | 1 | WRTS-1 | 76 | WRTS-1 | MEGPTCL | Twin ACSR Moose | 517.1749 | 42.18 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420 | Wardha | Koradi-II | 1 | MSETCL | 67 | WRTS-1 | MSEGCL | Quad ACSR Moose | 680.6549 | 49.044 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421 | Warora | Chandrapur-II | 1 | MEGPTCL | 45 | MEGPTCL | MSETCL | Twin ACSR Moose | 517.1749 | 24.975 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
422 | Warora | Chandrapur-II | 2 | MEGPTCL | 45 | MEGPTCL | MSETCL | Twin ACSR Moose | 517.1749 | 24.975 | - | - | - | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
423 | Zerda(Kansari) | Bhinmal | 1 | WRTS-2/NRTS-1 | 143 | GETCO | NRTS-1 | Twin ACSR Moose | 517.1749 | 79.365 | 50 | - | 50 | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
424 | Zerda(Kansari) | Kankroli | 1 | WRTS-2/NRTS-1 | 234 | GETCO | NRTS-1 | Twin ACSR Moose | 517.1749 | 129.87 | 50 | - | - | - | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
425 | Zerda(Kansari) | Varsana | 1 | GETCO | 258 | GETCO | GETCO | Twin ACSR Moose | 517.1749 | 143.19 | 63 | - | - | - | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Future | Total |  |  | 54744.8 | [5 empty] | 5443 |  | 6011 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 30181.839 | [9 empty] | 0 | 64 | 0 | 15 | 0 | 5 | 0 | 64 | 0 | 23 | 0 | 4
[20 empty] | 0 | 3200 | 0 | 945 | 0 | 400 | 0 | 3200 | 0 | 1449 | 0 | 320
[22 empty] | 4545 | [5 empty] | 4969
9514

## Summary 400 kV SS
S.No | S/S | Line Reactors | [5 empty] | Bus Reactors |  |  |  | Total LRs MVAR | Total BRs MVAR | Total S/W MVAR at SS | Total S/S MVAR Resources
|  | 50 MVAR |  | 63 MVAR |  | 80 MVAR |  | 50 MVAR | 63 MVAR | 80 MVAR | 125 MVAR
|  | S/W | Non S/W | S/W | Non S/W | S/W | Non S/W
1 | ACBIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Akola | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
3 | Akola(2) | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
4 | Alkud | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
5 | Amreli | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 175 | 175 | 175
6 | APL-Mundra | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 285 | 285 | 285
7 | Asoj | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 150 | 50 | 50 | 200
8 | Astha | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | MP
9 | Athena | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Aurangabad-M(Waluj) | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 150
11 | Aurangabad-PG | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 260 | 125 | 285 | 385
12 | Bableshwar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 160 | 160 | 160
13 | Bachau | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 126 | 188 | 188 | 314
14 | Balco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
15 | Betul | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 125 | 225 | 225
16 | Bhadrawati | 0 | 4 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 452 | 50 | 50 | 502
17 | Bhatapara | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 125 | 125 | 175
18 | Bhilai | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 330
19 | Bhopal-BDTCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
20 | Bhopal-MP | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 100 | 205 | 205 | 305 | MP
21 | Bhusawal (Khadka) | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150
22 | Bilaspur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Bina-MP | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150 | MP
24 | Bina-NHPTL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
25 | Bina-NTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
26 | Bina-PG | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 326 | 125 | 251 | 451 | MP
27 | Birsingpur | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 113 | 50 | 50 | 163 | MP
28 | Boisar | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 160
29 | CGPL | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 252 | 63 | 315 | 315
30 | Chakan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Champa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
32 | Chandrapur | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 150
33 | Chandrapur-GCR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | Chandrapur-II | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | Charnaka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
36 | Chhegaon | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50 | MP
37 | Chorania | 0 | 2 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 226 | 175 | 175 | 401
38 | Damoh | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 150 | 188 | 188 | 338 | MP
39 | DB-Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | Deepnagar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | Dehgam | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 100 | 188 | 188 | 288
42 | DGEN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
43 | Dhariwal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
44 | Dhariwal-MS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | Dhule-BDTCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
46 | Dhule-MS | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 200 | 80 | 180 | 280
47 | Ektuni (Aurangabad(3)) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | EMCO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80 | MP
49 | Essar_Mahan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80 | MP
50 | Gandhar | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 50 | 50 | 50 | 100
51 | GMR-CG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
52 | GPEC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | Gwalior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 375 | 375 | 375 | MP
54 | Hadala | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 63 | 175 | 175 | 238
55 | Hazira | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | IEPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | Indira Sagar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
58 | Indore-MP | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 250 | MP
59 | Indore-PG | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 100 | 188 | 288 | 288 | MP
60 | Itarsi | 2 | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 400 | 300 | 400 | 700 | MP
61 | Jabalpur | 2 | 2 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 1 | 452 | 188 | 288 | 640 | MP
62 | Jabalpur (PS) | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 250 | 250 | 350 | MP
63 | Jagdalpur | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 80 | 80
64 | Jaigad | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 100 | 100 | 100
65 | Jejuri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | Jetpur | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 126 | 113 | 113 | 239 | MP
67 | Jhabua Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
68 | JP-Bina | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | JPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
70 | JPL_extn(Tamnar) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
71 | JP-Nigrie | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
72 | Julwania | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
73 | Kala | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
74 | Kalwa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | Karad | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 80 | 80 | 80 | 160
76 | Kasor | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 100 | 175 | 175 | 275 | MP
77 | Katni | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
78 | Khandwa | 0 | 4 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 360 | 250 | 410 | 610
79 | Khaparkheda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | Kharghar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
81 | Kolhapur | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
82 | Kolhapur-PG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
83 | Koradi | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150
84 | Koradi-II | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | Korba (W) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | Korba (W)-Ext | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | Korba-NTPC | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
88 | Kosamba | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 126 | 80 | 80 | 206
89 | Koyna stage-IV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | KSK Mahanadi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | KWPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | Lara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | Lonikhand | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 50 | 50 | 50 | 100
94 | Lonikhand-II | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
95 | Magarawada | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80 | MP
96 | Malwa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | Mansar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 63 | 63 | 63
98 | Mapusa | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
99 | Marwa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
100 | MB Power | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 125 | 225 | 225
101 | MCCPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | Mouda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 160 | 160 | 160 | MP
103 | Nagda | 0 | 4 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 200 | 100 | 100 | 300
104 | Nagothane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
105 | Nanded | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | Nandgaonpeth | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
107 | Navsari | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 63 | 63 | 63
108 | New koyna | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | Nicol-II | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | NSPCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | Padghe | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 50 | 80 | 80 | 130
112 | Parli-M | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 300 | 50 | 50 | 350 | MP
113 | Parli-PG | 0 | 2 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 1 | 352 | 188 | 188 | 540
114 | Pathadi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | Pirana-PG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
116 | Pirana-T | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100
117 | Pithampur | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
118 | Pune-PG | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 200 | 50 | 250 | 250
119 | Pune-PG(Shikrapur) | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 100 | 200
120 | Raigarh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 188 | 188 | 188
121 | Raigarh-PS(Kotra) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
122 | Raipur | 1 | 4 | 0 | 7 | 0 | 1 | 0 | 0 | 1 | 1 | 771 | 205 | 255 | 976
123 | Raipur-PS(Durg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
124 | Raita | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | Rajgarh | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 125 | 225 | 225
126 | Ranchodpura | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 100 | 175 | 175 | 275
127 | RGPPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | RKM | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | MP
129 | Sami | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 100 | 50 | 50 | 150 | MP
130 | Sasan | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50 | MP
131 | Satna | 0 | 8 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 400 | 113 | 113 | 513 | MP
132 | Satpura | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 50 | 126 | 126 | 176
133 | Seoni | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 210 | 250 | 250 | 460 | MP
134 | Sholapur-M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | Shujalpur | 0 | 4 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 326 | 188 | 314 | 514
136 | Sipat | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 160
137 | SKS | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 50 | 50 | 50
138 | Soja | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 130 | 130 | 130
139 | Solapur-NTPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
140 | Solapur-PG | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 100 | 63 | 63 | 163
141 | SSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | Sugen | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | Tamnar-PS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | Taptithanda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | Tarapur-3&4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | Tiroda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 160 | 160 | 160
147 | TRN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | Ukai | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | Uno-Sugen | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
150 | Vadinar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | Vadodara-PS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | Vandana | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 50
153 | Vapi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
154 | Varsana | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 175 | 175 | 175 | MP
155 | Veloda | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | MP
156 | Vindhyachal | 0 | 6 | 1 | 3 | 0 | 0 | 1 | 1 | 0 | 0 | 552 | 113 | 176 | 665 | MP
157 | Vindhyachal-III | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP
158 | Vindhyachal-IV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 80 | 80
159 | Vindhyachal-PS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 63 | 63 | 63
160 | Vindhyachal-V | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
161 | Wanakbori | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | Wardha | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 252 | 50 | 50 | 302
163 | Warora | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 125 | 125 | 125
164 | Zerda(Kansari) | 0 | 2 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 226 | 175 | 175 | 401
| Total | 21 | 125 | 9 | 38 | 5 | 9 | 36 | 18 | 29 | 48 | 11381 | 11254 | 13271 | 22635

## 400 kV BRs
S.No | Substation | Owner | Nos of Reactor | Total MVAR | Rated Voltage |  | 50 MVAR | 63 MVAR | 80 MVAR | 125 MVAR
1 | Alkud | MSETCL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
2 | Amreli | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175 | 0
3 | APL-Mundra | APL | 2X80 + 1X125 | 285 | 420 |  |  |  | 2 | 1 | 285 | 0
4 | Asoj | GETCO | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
5 | Astha | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
6 | Aurangabad-PG | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
7 | Bableshwar | MSETCL | 2X80 | 160 | 420 |  |  |  | 2 |  | 160 | 0
8 | Bachau | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
9 | Betul | PGCIL | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
10 | Bhadrawati | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
11 | Bhatapara | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
12 | Bhopal-BDTCL | BDTCL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
13 | Bhopal-MP | MPPTCL | 1X125 + 1x80 | 205 | 420 | 80 added |  |  | 1 | 1 | 205 | 0
14 | Bhusawal (Khadka) | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
15 | Bina-MP | MPPTCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
16 | Bina-PG | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
17 | Birsingpur | MPPGCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
18 | CGPL | CGPL | 1x63 | 63 | 420 |  |  | 1 |  |  | 63 | 0
19 | Champa | PGCIL | 1x80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
20 | Charnaka | GETCO | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
21 | Chhegaon | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
22 | Chorania | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175 | 0
23 | Damoh | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
24 | Dehgam | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
25 | DGEN | DGEN | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
26 | Dhariwal | DIL | 1x80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
27 | Dhule-MS | PGCIL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
28 | EMCO | GMR | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
29 | Essar_Mahan | ESSAR | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
30 | Gandhar | NTPC | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
31 | GMR-CG | GMR | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
32 | Gwalior | PGCIL | 3X125 | 375 | 420 |  |  |  |  | 3 | 375 | 0
33 | Hadala | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175 | 0
34 | Indore-PG | PGCIL | 1X125 + 1X63 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
35 | Itarsi | PGCIL | 2X125 + 1X50 | 300 | 420 |  | 1 |  |  | 2 | 300 | 0
36 | Jabalpur | PGCIL | 1X125 + 1X63 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
37 | Jabalpur (PS) | PGCIL | 2X125 | 250 | 420 |  |  |  |  | 2 | 250 | 0
38 | Jaigad | JPTL | 2x50 | 100 | 420 |  | 2 |  |  |  | 100 | 0
39 | Jetpur | GETCO | 1X50 + 1X63 | 113 | 420 |  | 1 | 1 |  |  | 113 | 0
40 | Jhabua Power | Jhabua | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
41 | JPL | JPL | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
42 | JP-Nigrie | JPVL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
43 | Julwania | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
44 | Kala | PGCIL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
45 | Karad | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
46 | Kasor | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175 | 0
47 | Khandwa | PGCIL | 2X125 | 250 | 420 |  |  |  |  | 2 | 250 | 0
48 | Kharghar | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
49 | Kolhapur | PGCIL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
50 | Kolhapur-PG | PGCIL | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
51 | Koradi | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
52 | Kosamba | GETCO | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
53 | Lonikhand | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
54 | Magarawada | PGCIL | 1x80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
55 | Mansar | GETCO | 1x63 | 63 | 420 | 80 |  | 1 |  |  | 63 | 0
56 | Mapusa | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
57 | MB Power | MB Power | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
58 | Mouda | NTPC | 2x80 | 160 | 420 |  |  |  | 2 |  | 160 | 0
59 | Nagda | MPPTCL | 2X50 | 100 | 420 |  | 2 |  |  |  | 100 | 0
60 | Nagothane | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
61 | Nandgaonpeth | Rattan India | 1x80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
62 | Navsari | PGCIL | 1X63 | 63 | 420 |  |  | 1 |  |  | 63 | 0
63 | Padghe | MSETCL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
64 | Parli-M | MSETCL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
65 | Parli-PG | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
66 | Pirana-PG | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
67 | Pithampur | MPPTCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
68 | Pune-PG | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
69 | Raigarh | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
70 | Raigarh-PS(Kotra) | PGCIL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
71 | Raipur | PGCIL | 1X125 + 1X80 | 205 | 420 |  |  |  | 1 | 1 | 205 | 0
72 | Rajgarh | PGCIL | 1X125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
73 | Ranchodpura | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175 | 0
74 | RKM | RKM | 2x50 | 100 | 420 |  | 2 |  |  |  | 100 | 0
75 | Sami | APL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
76 | Satna | PGCIL | 1X50 + 1X63 | 113 | 420 |  | 1 | 1 |  |  | 113 | 0
77 | Satpura | MPPTCL | 2X63 | 126 | 420 |  |  | 2 |  |  | 126 | 0
78 | Seoni | PGCIL | 1x125+1x125 | 250 | 420 |  |  |  |  | 2 | 250 | 0
79 | Shujalpur | PGCIL | 1X63 + 1X125 | 188 | 420 |  |  | 1 |  | 1 | 188 | 0
80 | SKS | SPGCL | 1x50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
81 | Soja | GETCO | 1X50 + 1X80 | 130 | 420 |  | 1 |  | 1 |  | 130 | 0
82 | Solapur-NTPC | NTPC | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
83 | Solapur-PG | PGCIL | 1X63 | 63 | 420 |  |  | 1 |  |  | 63 | 0
84 | Tiroda | APML | 2X80 | 160 | 420 |  |  |  | 2 |  | 160 | 0
85 | Uno-Sugen | TPL | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
86 | Varsana | GETCO | 1X50 + 1X125 | 175 | 420 |  | 1 |  |  | 1 | 175 | 0
87 | Veloda | GETCO | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
88 | Vindhyachal | NTPC | 1X63 + 1X50 | 113 | 420 |  | 1 | 1 |  |  | 113 | 0
89 | Vindhyachal-IV | NTPC | 1X80 | 80 | 420 |  |  |  | 1 |  | 80 | 0
90 | Vindhyachal-PS | PGCIL | 1X63 | 63 | 420 |  |  | 1 |  |  | 63 | 0
91 | Vindhyachal-V | NTPC | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
92 | Wardha | PGCIL | 1X50 | 50 | 420 |  | 1 |  |  |  | 50 | 0
93 | Warora | ATIL | 1x125 | 125 | 420 |  |  |  |  | 1 | 125 | 0
94 | Zerda(Kansari) | GETCO | 1X50 + 1X125 | 175 | 420 | only 50 | 1 |  |  | 1 | 175 | 0
| * Future | Total | 50x34+18x63+28x80+48x125 | 11254 |  |  | 36 | 18 | 29 | 48 | 11254
[7 empty] | 1800 | 1134 | 2320 | 6000 | 11254
0

## Summary 765 kV SS
S.No | S/S | Line Reactors |  |  |  | Bus Reactors |  | Total LRs MVAR | Total BRs MVAR | Total S/W MVAR at S/S | Total S/S MVAR Resources
|  | 240 MVAR |  | 330 MVAR |  | 240 MVAR | 330 MVAR
|  | S/W | Non S/W | S/W | Non S/W
1 | Akola(2) | 4 | 0 | 0 | 0 | 1 | 0 | 960 | 240 | 1200 | 1200 |  | 240 | 1
2 | Aurangabad-PG | 2 | 4 | 0 | 0 | 1 | 0 | 1440 | 240 | 720 | 1680 |  | 480 | 2
3 | Bhopal-BDTCL | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 | MP | 240 | 1
4 | Bilaspur | 3 | 0 | 0 | 0 | 1 | 0 | 720 | 240 | 960 | 960 |  | 240 | 1
5 | Bina-NHPTL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Bina-PG | 2 | 8 | 0 | 0 | 2 | 0 | 2400 | 480 | 960 | 2880 | MP | 480 | 2
7 | Champa | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 240 | 240 | 240 |  | 240 | 1
8 | Dharamjaygarh | 0 | 0 | 8 | 2 | 0 | 2 | 3300 | 660 | 3300 | 3960 |  | 660
9 | Dhule-BDTCL | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 | MP | 240 | 1
10 | Ektuni (Aurangabad(3)) | 0 | 2 | 0 | 0 | 1 | 0 | 480 | 240 | 240 | 720 |  | -
11 | Gadarwara | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MP | 240 | 1
12 | Gwalior | 5 | 2 | 0 | 0 | 1 | 0 | 1680 | 240 | 1440 | 1920 | MP | 480 | 2
13 | Indore-PG | 1 | 2 | 0 | 0 | 2 | 0 | 720 | 480 | 720 | 1200 | MP | 480 | 2
14 | Jabalpur-PS | 4 | 4 | 0 | 2 | 2 | 0 | 2580 | 480 | 1440 | 3060 |  | 240 | 1
15 | Kholpaur-PG# | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 1
16 | Koradi(III) | 4 | 0 | 0 | 0 | 1 | 0 | 960 | 240 | 1200 | 1200 |  | 240 | 1
17 | Pune-PG(Shikrapur) | 1 | 0 | 0 | 0 | 1 | 0 | 240 | 240 | 480 | 480 |  | 240 | 1
18 | Raigarh-PS(Kotra) | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 | MP | 240 | 1
19 | Raipur-PS(Durg) | 2 | 6 | 0 | 0 | 1 | 0 | 1920 | 240 | 720 | 2160 | MP | 480 | 2
20 | Sasan | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 | MP | 240 | 1
21 | Satna | 4 | 4 | 0 | 0 | 2 | 0 | 1920 | 480 | 1440 | 2400 |  | 240 | 1
22 | Seoni | 3 | 2 | 0 | 0 | 1 | 0 | 1200 | 240 | 960 | 1440 |  | 240 | 1
23 | Sipat | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 |  | 240 | 1
24 | Solapur | 5 | 0 | 0 | 0 | 1 | 0 | 1200 | 240 | 1440 | 1440 |  | 240 | 1
25 | Tamnar | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 240 | 240 | 240 |  | 240 | 1
26 | Tiroda | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720 | MP | 240 | 1
27 | Vadodora-PS | 0 | 2 | 0 | 0 | 1 | 0 | 480 | 240 | 240 | 720
28 | Vindhyachal-PS | 2 | 0 | 0 | 0 | 1 | 0 | 480 | 240 | 720 | 720
29 | Wardha | 0 | 4 | 4 | 4 | 1 | 1 | 3600 | 570 | 1890 | 4170 |  | 570 | 1
| Total | 54 | 40 | 12 | 8 | 29 | 3 | 29160 | 7950 | 24870 | 37110

## 765kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Km | Conductor Type | SIL (Uncompensated) | No Load MVAR Generated | End1 LR |  | End2 LR |  | End 1 Over Voltage Stage 1 | End 1 Over Voltage Stage 2 | End 2 Over Voltage Stage 1 | End 2 Over Voltage Stage 2 | Remarks | [5 empty] | End-1 |  |  |  | End-2
[11 empty] | MVAR | S/W | MVAR | S/W | [10 empty] | 240 MVAR SLR | 240 MVAR NSLR | 330 MVAR SLR | 330 MVAR NSLR | 240 MVAR SLR | 240 MVAR NSLR | 330 MVAR SLR | 330 MVAR NSLR
1 | Akola(2)* | Ektuni (Aurangabad(3)) | 2 | MEGPTCL | MEGPTCL | MSETCL | 219 | Quad Bersimis | 2194.4416 | 514.65 | 240 | Yes | 240 | - | [6 empty] | X | B | Zpu | Z(ohms) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
2 | Akola(2)* | Ektuni (Aurangabad(3)) | 1 | MEGPTCL | MEGPTCL | MSETCL | 219 | Quad Bersimis | 2194.4416 | 514.65 | 240 | Yes | 240 | - | [5 empty] | Quad Bersimis | 4.88e-05 | 0.0235 | 0.04557 | 266.6852 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
3 | Aurangabad-PG | Wardha* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 348 | Hexa Zebra | 2470.0035 | 925.68 | 240 | - | 330 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 330
4 | Aurangabad-PG | Wardha* | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 348 | Hexa Zebra | 2470.0035 | 925.68 | 240 | - | 330 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 330
5 | Aurangabad-PG | Wardha* | 3 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 240 | - | 330 | Yes | [5 empty] | Hexa Zebra | 4.36e-05 | 0.0266 | 0.040486 | 236.9329 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 330
6 | Aurangabad-PG | Wardha* | 4 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 240 | - | 330 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 330
7 | Aurangabad-PG* | Solapur-PG* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 279 | Hexa Zebra | 2470.0035 | 742.14 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
8 | Aurangabad-PG* | Solapur-PG* | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 279 | Hexa Zebra | 2470.0035 | 742.14 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
9 | Bhopal-BDTCL* | Indore-PG* | 1 | BDTCL | BDTCL | WRTS-2 | 176 | Quad Bersimis | 2194.4416 | 413.6 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
10 | Bilaspur* | Seoni | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 333 | Quad Bersimis | 2194.4416 | 782.55 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
11 | Bilaspur* | Seoni | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 335 | Quad Bersimis | 2194.4416 | 787.25 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
12 | Bilaspur* | Dharamjaygarh | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 89 | Quad Bersimis | 2194.4416 | 209.15 | 240 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | -
13 | Bina-PG | Bina-NHPTL | 1 | WRTS-2 | WRTS-2 | NHPTL | 0.2 | Quad Bersimis | 2194.4416 | 0.47 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
14 | Bina-PG* | Gwalior* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 235 | Quad Bersimis | 2194.4416 | 552.25 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
15 | Bina-PG* | Gwalior* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 235 | Quad Bersimis | 2194.4416 | 552.25 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
16 | Bina-PG* | Gwalior* | 3 | WRTS-2 | WRTS-2 | WRTS-2 | 231 | Quad Bersimis | 2194.4416 | 542.85 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
17 | Bina-PG* | Indore-PG* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 310 | Quad Bersimis | 2194.4416 | 728.5 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
18 | Bina-PG* | Jabalpur-PS* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 230 | Quad Bersimis | 2194.4416 | 540.5 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
19 | Bina-PG* | Jabalpur-PS* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 230 | Quad Bersimis | 2194.4416 | 540.5 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
20 | Bina-PG* | Jabalpur-PS* | 3 | JTCL | WRTS-2 | WRTS-2 | 236 | Quad Bersimis | 2194.4416 | 554.6 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
21 | Champa | Dharamjaygarh | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 56 | Quad Bersimis | 2194.4416 | 131.6 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
22 | Dharamjaygarh | Ranchi | 1 | ERTS-1/WRTS-1 | WRTS-1 | ERTS-1 | 303 | Quad Bersimis | 2194.4416 | 712.05 | 330 | - | 240 | Yes | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 330 | 240
23 | Dharamjaygarh | Ranchi | 2 | ERTS-1/WRTS-1 | WRTS-1 | ERTS-1 | 354 | Quad Bersimis | 2194.4416 | 831.9 | 330 | - | 240 | Yes | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 330 | 240
24 | Dharamjaygarh* | Jharsuguda | 1 | WRTS-1 | WRTS-1 | ERTS-2 | 151 | Hexa Zebra | 2470.0035 | 401.66 | 330 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 330 | -
25 | Dharamjaygarh* | Jharsuguda | 2 | WRTS-1 | WRTS-1 | ERTS-2 | 151 | Hexa Zebra | 2470.0035 | 401.66 | 330 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 330 | -
26 | Dharamjaygarh* | Jabalpur-PS* | 1 | WRTS-1 | WRTS-1 | WRTS-2 | 424 | Hexa Zebra | 2470.0035 | 1127.84 | 330 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 330 | 240
27 | Dharamjaygarh* | Jabalpur-PS* | 2 | WRTS-1 | WRTS-1 | WRTS-2 | 424 | Hexa Zebra | 2470.0035 | 1127.84 | 330 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 330 | 240
28 | Dharamjaygarh* | Jabalpur-PS* | 3 | JTCL | WRTS-1 | WRTS-2 | 379 | Hexa Zebra | 2470.0035 | 1008.14 | 330 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 330 | 240
29 | Dharamjaygarh* | Jabalpur-PS* | 4 | JTCL | WRTS-1 | WRTS-2 | 379 | Hexa Zebra | 2470.0035 | 1008.14 | 330 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 330 | 240
30 | Dharamjaygarh*^ | Jharsuguda^ | 3 | WRTS-1 | WRTS-1 | ERTS-2 | 303 | Hexa Zebra | 2470.0035 | 805.98 | 330 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 330 | -
31 | Dharamjaygarh*^ | Jharsuguda^ | 4 | WRTS-1 | WRTS-1 | ERTS-2 | 303 | Hexa Zebra | 2470.0035 | 805.98 | 330 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 330 | -
32 | Dhule-BDTCL* | Aurangabad-PG | 1 | BDTCL | BDTCL | WRTS-I | 192 | Quad Bersimis | 2194.4416 | 451.2 | 240 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | -
33 | Gwalior | Agra | 1 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 129 | Quad Bersimis | 2194.4416 | 303.15 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
34 | Gwalior | Agra | 2 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 128 | Quad Bersimis | 2194.4416 | 300.8 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
35 | Gwalior* | Jaipur | 1 | NRTS-1/WRTS-2 | WRTS-2 | RRVPNL | 304 | Quad Bersimis | 2194.4416 | 714.4 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
36 | Gwalior* | Jaipur | 2 | NRTS-1/WRTS-2 | WRTS-2 | RRVPNL | 311 | Quad Bersimis | 2194.4416 | 730.85 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
37 | Jabalpur (PS) | Gadarwara | 1 | WRTS-2 | WRTS-2 | NTPC | 102 | Hexa Zebra | 2470.0035 | 271.32 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
38 | Jabalpur (PS) | Gadarwara | 2 | WRTS-2 | WRTS-2 | NTPC | 102 | Hexa Zebra | 2470.0035 | 271.32 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
39 | Jabalpur-PS* | Bhopal-BDTCL* | 1 | BDTCL | WRTS-2 | BDTCL | 260 | Quad Bersimis | 2194.4416 | 611 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
40 | Jabalpur-PS^ | Orai^ | 1 | WRTS-2/NRTS-2 | WRTS-2 | NRTS-2 | 360 | Hexa Zebra | 2470.0035 | 957.6 | 330 | - | - | - | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 330 | -
41 | Jabalpur-PS^ | Orai^ | 2 | WRTS-2/NRTS-2 | WRTS-2 | NRTS-2 | 360 | Hexa Zebra | 2470.0035 | 957.6 | 330 | - | - | - | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 330 | -
42 | Kholpaur-PG# | Kudgi# | 1 | WRTS-1 | WRTS-1 | SRTS-1 | 191 | Hexa Zebra | 2470.0035 | 508.06 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
43 | Kholpaur-PG# | Kudgi# | 2 | WRTS-1 | WRTS-1 | SRTS-1 | 191 | Hexa Zebra | 2470.0035 | 508.06 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
44 | Koradi(III) | Akola(2)* | 1 | MEGPTCL | MEGPTCL | MEGPTCL | 222 | Quad Bersimis | 2194.4416 | 521.7 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
45 | Koradi(III) | Akola(2)* | 2 | MEGPTCL | MEGPTCL | MEGPTCL | 222 | Quad Bersimis | 2194.4416 | 521.7 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
46 | Pune-PG (Shikrapur)* | Solapur-PG* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 270 | Quad Bersimis | 2194.4416 | 634.5 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
47 | Raigarh-PS(Kotra) | Raipur-PS(Durg) | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 235 | Hexa Zebra | 2470.0035 | 625.1 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
48 | Raigarh-PS(Kotra) | Tamnar | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 48 | Hexa Zebra | 2470.0035 | 127.68 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
49 | Raigarh-PS(Kotra) | Tamnar | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 48 | Hexa Zebra | 2470.0035 | 127.68 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
50 | Raigarh-PS(Kotra) | Champa | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 96 | Quad Bersimis | 2194.4416 | 225.6 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
51 | Raigarh-PS(Kotra)* | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 235 | Hexa Zebra | 2470.0035 | 625.1 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
52 | Raipur-PS(Durg) | Champa | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 153 | Hexa Zebra | 2470.0035 | 406.98 | 240 | - | - | - | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | -
53 | Raipur-PS(Durg) | Champa | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 150 | Hexa Zebra | 2470.0035 | 399 | 240 | - | - | - | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | -
54 | Sasan | Satna* | 1 | WRTS-2 | SPL | WRTS-2 | 246 | Quad Bersimis | 2194.4416 | 578.1 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
55 | Sasan | Satna* | 2 | WRTS-2 | SPL | WRTS-2 | 243 | Quad Bersimis | 2194.4416 | 571.05 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
56 | Sasan | Vindhyachal-PS | 1 | WRTS-2 | SPL | WRTS-2 | 6 | Quad Bersimis | 2194.4416 | 14.1 | - | - | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | -
57 | Satna* | Gwalior* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 337 | Quad Bersimis | 2194.4416 | 791.95 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
58 | Satna* | Gwalior* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 337 | Quad Bersimis | 2194.4416 | 791.95 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
59 | Satna* | Bina-PG* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 274 | Quad Bersimis | 2194.4416 | 643.9 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
60 | Satna* | Bina-PG* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 276 | Quad Bersimis | 2194.4416 | 648.6 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
61 | Satna* | Vindhyachal-PS* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 237 | Quad Bersimis | 2194.4416 | 556.95 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
62 | Satna* | Vindhyachal-PS* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 237 | Quad Bersimis | 2194.4416 | 556.95 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
63 | Seoni* | Bina-PG* | 1 | WRTS-1 | WRTS-1 | WRTS-2 | 292 | Quad Bersimis | 2194.4416 | 686.2 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
64 | Seoni* | Wardha | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 261 | Quad Bersimis | 2194.4416 | 613.35 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
65 | Seoni* | Wardha | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 261 | Quad Bersimis | 2194.4416 | 613.35 | 240 | Yes | 240 | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 240 | 240
66 | Sipat | Bilaspur | 1 | WRTS-1 | NTPC | WRTS-1 | 22 | Quad Bersimis | 2194.4416 | 51.7 | 240 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | -
67 | Sipat | Bilaspur | 2 | WRTS-1 | NTPC | WRTS-1 | 22 | Quad Bersimis | 2194.4416 | 51.7 | 240 | Yes | - | - | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | -
68 | Solapur* | Raichur | 1 | RSTCL | WRTS-1 | SRTS-1 | 208 | Quad Bersimis | 2194.4416 | 488.8 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
69 | Solapur* | Raichur | 2 | RSTCL | WRTS-1 | SRTS-1 | 208 | Quad Bersimis | 2194.4416 | 488.8 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
70 | Tiroda* | Koradi(III) | 1 | MEGPTCL | APML | MEGPTCL | 136 | Quad Bersimis | 2194.4416 | 319.6 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 240 | 240
71 | Tiroda* | Koradi(III) | 2 | MEGPTCL | APML | MEGPTCL | 138 | Quad Bersimis | 2194.4416 | 324.3 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 240
72 | Vadodora-PS | Indore-PG* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 293 | Quad Bersimis | 2194.4416 | 688.55 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
73 | Vadodora-PS | Dhule-BDTCL* | 1 | BDTCL | WRTS-2 | BDTCL | 268 | Quad Bersimis | 2194.4416 | 629.8 | 240 | - | 240 | Yes | [10 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
74 | Wardha | Raipur-PS(Durg)* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 377 | Hexa Zebra | 2470.0035 | 1002.82 | 330 | - | 240 | Yes | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
75 | Wardha | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 377 | Hexa Zebra | 2470.0035 | 1002.82 | 330 | - | 240 | Yes | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
76 | Wardha | Raipur-PS(Durg)* | 3 | WRTS-1 | WRTS-1 | WRTS-1 | 361 | Hexa Zebra | 2470.0035 | 960.26 | 330 | - | 240 | Yes | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
77 | Wardha | Raipur-PS(Durg)* | 4 | WRTS-1 | WRTS-1 | WRTS-1 | 361 | Hexa Zebra | 2470.0035 | 960.26 | 330 | - | 240 | Yes | [10 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
78 | Wardha* | Nizamabad | 1 | WRTS-1/ SRTS-1 | WRTS-1 | SRTS-1 | 291 | Hexa Zebra | 2470.0035 | 774.06 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | Wardha* | Nizamabad | 2 | WRTS-1/ SRTS-1 | WRTS-1 | SRTS-1 | 291 | Hexa Zebra | 2470.0035 | 774.06 | 240 | Yes | 240 | Yes | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# 765 kV line charged at 400 kV, * Can be converted as BR by Bypassing NGR Manually, ^ Future Line |  |  |  | Total |  |  | 18968.2 |  |  |  | 17520 |  | 13560 | [11 empty] | 0 | 15 | 0 | 8 | 0 | 23 | 0 | 0
[25 empty] | 0 | 3600 | 0 | 2640 | 0 | 5520 | 0 | 0
[27 empty] | 6240 |  |  |  | 5520
31080
11760
7950
19710

## 765 kV SS Res
Sr. No. | Name of S/S | S/S Owner | Lines | ID | km | Conductor Type | LRs | LRs S/W | BRs | Total MVAR | Rated Voltage | 240 MVAR SLRs | 240 MVAR NSLRs | 330 MVAR SLRs | 330 MVAR NSLRs
1 | Akola(2) | MEGPTCL | Ektuni (Aurangabad(3))* | 2 | 219 | Quad Bersimis | 240 | Yes | 1x240 | MEGPTCL | MSETCL | 1 | 0 | 0 | 0
|  |  | Ektuni (Aurangabad(3))* | 1 | 219 | Quad Bersimis | 240 | Yes |  | MEGPTCL | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Koradi(III)* | 1 | 222 | Quad Bersimis | 240 | Yes |  | MEGPTCL | MEGPTCL | 1 | 0 | 0 | 0
|  |  | Koradi(III)* | 2 | 222 | Quad Bersimis | 240 | Yes |  | MEGPTCL | MEGPTCL | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 960 |  | 240 |  |  | 4 | 0 | 0 | 0 | 960 | 0
2 | Aurangabad-PG | PGCIL | Wardha | 1 | 348 | Hexa Zebra | 240 | - | 1x240 | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha | 2 | 348 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha | 3 | 370 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha | 4 | 370 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Solapur-PG* | 1 | 279 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Solapur-PG* | 2 | 279 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Dhule-BDTCL | 1 | 192 | Quad Bersimis | - | - |  | BDTCL | BDTCL | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1440 |  | 240 |  |  | 2 | 4 | 0 | 0 | 1440 | 0
3 | Bhopal-BDTCL | BDTCL | Indore-PG* | 1 | 176 | Quad Bersimis | 240 | Yes | 1x240 | BDTCL | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Jabalpur-PS* | 1 | 260 | Quad Bersimis | 240 | Yes |  | BDTCL | WRTS-2 | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480 | 0
4 | Bilaspur | PGCIL | Seoni* | 1 | 333 | Quad Bersimis | 240 | Yes | 1x240 | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Seoni* | 2 | 335 | Quad Bersimis | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Dharamjaygarh* | 1 | 89 | Quad Bersimis | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Sipat | 1 | 22 | Quad Bersimis | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0
|  |  | Sipat | 2 | 22 | Quad Bersimis | - | - |  | WRTS-1 | NTPC | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 720 |  | 240 |  |  | 3 | 0 | 0 | 0 | 720 | 0
5 | Bina-NHPTL | NHPTL | Bina-PG | 1 | 0.2 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | - | - | - |  |  | 0 | 0 | 0 | 0
6 | Bina-PG | PGCIL | Gwalior* | 1 | 235 | Quad Bersimis | 240 | - | 2x240 | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Gwalior* | 2 | 235 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Gwalior* | 3 | 231 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Indore-PG* | 1 | 310 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Jabalpur-PS* | 1 | 230 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Jabalpur-PS* | 2 | 230 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Jabalpur-PS* | 3 | 236 | Quad Bersimis | 240 | - |  | JTCL | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Bina-NHPTL | 1 | 0.2 | Quad Bersimis | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0
|  |  | Satna* | 1 | 274 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Satna* | 2 | 276 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Seoni* | 1 | 292 | Quad Bersimis | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 2400 |  | 480 |  |  | 2 | 8 | 0 | 0 | 2400 | 0
7 | Champa | PGCIL | Dharamjaygarh | 1 | 56 | Quad Bersimis | - | - | 1x240 |  |  | 0 | 0 | 0 | 0
|  |  | Raigarh-PS(Kotra) | 1 | 96 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Raipur-PS(Durg) | 1 | 153 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Raipur-PS(Durg) | 2 | 150 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR | [6 empty] | 240 |  |  | 0 | 0 | 0 | 0 | 0 | 0
8 | Dharamjaygarh | PGCIL | Ranchi | 1 | 301 | Quad Bersimis | 330 | - | 2x330 |  |  | 0 | 0 | 0 | 1
|  |  | Ranchi | 2 | 303 | Quad Bersimis | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Jharsuguda* | 1 | 303 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jharsuguda* | 2 | 303 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jharsuguda^ | 3 | 303 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jharsuguda^ | 4 | 303 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS* | 1 | 424 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS* | 2 | 424 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS* | 3 | 379 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Jabalpur-PS* | 4 | 379 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Bilaspur | 1 | 89 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Champa | 1 | 56 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 3300 |  | 660 |  |  | 0 | 0 | 8 | 2 | 3300 | 0
9 | Dhule-BDTCL | BDTCL | Aurangabad-PG* | 1 | 192 | Quad Bersimis | 240 | Yes | 240 |  |  | 1 | 0 | 0 | 0
|  |  | Vadodora-PS * | 1 | 268 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480 | 0
10 | Ektuni (Aurangabad(3)) | MSETCL | Akola(2) | 2 | 219 | Quad Bersimis | 240 | - | 240 |  |  | 0 | 1 | 0 | 0
|  |  | Akola(2) | 1 | 219 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 0 | 2 | 0 | 0 | 480 | 0
11 | Gadarwara | NTPC | Jabalpur (PS) | 1 | 102 | Hexa Zebra | - | - | - |  |  | 0 | 0 | 0 | 0
|  |  | Jabalpur (PS) | 2 | 102 | Hexa Zebra | - | - | - |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | - | - | - |  |  | 0 | 0 | 0 | 0
12 | Gwalior | PGCIL | Agra | 1 | 129 | Quad Bersimis | - | - | 240 |  |  | 0 | 0 | 0 | 0
|  |  | Agra | 2 | 128 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Jaipur* | 1 | 304 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Jaipur* | 2 | 311 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Bina-PG* | 1 | 235 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Bina-PG* | 2 | 235 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Bina-PG* | 3 | 231 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Satna* | 1 | 337 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Satna* | 2 | 337 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 1680 |  | 240 |  |  | 5 | 2 | 0 | 0 | 1680 | 0
13 | Indore-PG | PGCIL | Bhopal-BDTCL* | 1 | 176 | Quad Bersimis | 240 | - | 2x240 |  |  | 0 | 1 | 0 | 0
|  |  | Bina-PG* | 1 | 310 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Vadodora-PS * | 1 | 293 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 720 |  | 480 |  |  | 1 | 2 | 0 | 0 | 720 | 0
14 | Jabalpur-PS | PGCIL | Bina-PG* | 1 | 230 | Quad Bersimis | 240 | Yes | 2x240 | 480 | 800 | 1 | 0 | 0 | 0
|  |  | Bina-PG* | 2 | 230 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Bina-PG* | 3 | 236 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Dharamjaygarh* | 1 | 424 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Dharamjaygarh* | 2 | 424 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Dharamjaygarh* | 3 | 379 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Dharamjaygarh* | 4 | 379 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Bhopal-BDTCL* | 1 | 260 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Orai^ | 1 | 360 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Orai^ | 2 | 360 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  | Total MVAR |  |  |  |  | 2580 |  | 480 |  |  | 4 | 4 | 0 | 2 | 2580 | 0
15 | Kholpaur-PG# | PGCIL | Kudgi# | 1 | 191 | Hexa Zebra | - | - | - |  |  | 0 | 0 | 0 | 0
|  |  | Kudgi# | 2 | 191 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | - |  | - |  |  | 0 | 0 | 0 | 0 | 0
16 | Koradi(III) | MEGPTCL | Akola(2) | 1 | 222 | Quad Bersimis | 240 | Yes | 1x240 |  |  | 1 | 0 | 0 | 0
|  |  | Akola(2) | 2 | 222 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Tiroda | 1 | 136 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Tiroda | 2 | 138 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 960 |  | 240 |  |  | 4 | 0 | 0 | 0 | 960 | 0
17 | Pune-PG(Shikrapur) | PGCIL | Solapur* | 1 | 270 | Quad Bersimis | 240 | Yes | 1x240 |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 240 |  | 240 |  |  | 1 | 0 | 0 | 0 | 240 | 0
18 | Raigarh-PS(Kotra) | PGCIL | Raipur-PS(Durg) | 1 | 235 | Hexa Zebra | 240 | Yes | 1x240 |  |  | 1 | 0 | 0 | 0
|  |  | Raipur-PS(Durg)* | 2 | 235 | Hexa Zebra | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Tamnar | 1 | 48 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Tamnar | 2 | 48 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  |  | Champa | 1 | 96 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480 | 0
19 | Raipur-PS(Durg) | PGCIL | Champa | 1 | 153 | Hexa Zebra | 240 | - | 1x240 | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Champa | 2 | 150 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Raigarh-PS(Kotra) | 1 | 235 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Raigarh-PS(Kotra) | 2 | 235 | Hexa Zebra | 240 | - |  | WRTS-1 | WRTS-1 | 0 | 1 | 0 | 0
|  |  | Wardha* | 1 | 370 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Wardha | 2 | 370 | Hexa Zebra | 240 | Yes |  | WRTS-1 | WRTS-1 | 1 | 0 | 0 | 0
|  |  | Wardha | 3 | 361 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Wardha | 4 | 361 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 1920 |  | 240 |  |  | 2 | 6 | 0 | 0 | 1920 | 0
20 | Sasan | SPL | Satna | 1 | 246 | Quad Bersimis | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Satna | 2 | 243 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Vindhyachal-PS | 1 | 6 | Quad Bersimis | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480 | 0
21 | Satna | PGCIL | Gwalior* | 1 | 337 | Quad Bersimis | 240 | Yes | 2x240 | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Gwalior* | 2 | 337 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Bina-PG* | 1 | 274 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Bina-PG* | 2 | 276 | Quad Bersimis | 240 | Yes |  | WRTS-2 | WRTS-2 | 1 | 0 | 0 | 0
|  |  | Vindhyachal-PS* | 1 | 237 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Vindhyachal-PS* | 2 | 237 | Quad Bersimis | 240 | - |  | WRTS-2 | WRTS-2 | 0 | 1 | 0 | 0
|  |  | Sasan* | 1 | 246 | Quad Bersimis | 240 | - |  | WRTS-2 | SPL | 0 | 1 | 0 | 0
|  |  | Sasan* | 2 | 243 | Quad Bersimis | 240 | - |  | WRTS-2 | SPL | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 1920 |  | 480 |  |  | 4 | 4 | 0 | 0 | 1920 | 0
22 | Seoni | PGCIL | Bilaspur | 1 | 333 | Quad Bersimis | 240 | - | 1x240 | 240 | 800 | 0 | 1 | 0 | 0
|  |  | Bilaspur | 2 | 335 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Bina-PG* | 1 | 292 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Wardha* | 1 | 261 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Wardha* | 2 | 261 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1200 |  | 240 |  |  | 3 | 2 | 0 | 0 | 1200 | 0
23 | Sipat | NTPC | Bilaspur | 1 | 22 | Quad Bersimis | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Bilaspur | 2 | 22 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480 | 0
24 | Solapur | PGCIL | Aurangabad-PG* | 1 | 279 | Hexa Zebra | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Aurangabad-PG* | 2 | 279 | Hexa Zebra | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Pune-PG(Shikrapur)* | 1 | 270 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Raichur* | 1 | 208 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Raichur* | 2 | 208 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 1200 |  | 240 |  |  | 5 | 0 | 0 | 0 | 1200 | 0
25 | Tamnar | PGCIL | Raigarh-PS(Kotra) | 1 | 48 | Hexa Zebra | - | - | 1x240 | 240 | 800 | 0 | 0 | 0 | 0
|  |  | Raigarh-PS(Kotra) | 2 | 48 | Hexa Zebra | - | - |  |  |  | 0 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | - |  | 240 |  |  | 0 | 0 | 0 | 0 | 0 | #VALUE!
26 | Tiroda | APML | Koradi(III)* | 1 | 136 | Quad Bersimis | 240 | Yes | 1x240 | 240 | 800 | 1 | 0 | 0 | 0
|  |  | Koradi(III)* | 2 | 138 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480 | 0
27 | Vadodora-PS | PGCIL | Indore-PG | 1 | 293 | Quad Bersimis | 240 | - | 1x240 | 240 | 800 | 0 | 1 | 0 | 0
|  |  | Dhule-BDTCL | 1 | 268 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 0 | 2 | 0 | 0 | 480 | 0
28 | Vindhyachal-PS | PGCIL | Sasan | 1 | 6 | Quad Bersimis | - | - | 1x240 | 240 | 800 | 0 | 0 | 0 | 0
|  |  | Satna* | 1 | 237 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  |  | Satna* | 2 | 237 | Quad Bersimis | 240 | Yes |  |  |  | 1 | 0 | 0 | 0
|  | Total MVAR |  |  |  |  | 480 |  | 240 |  |  | 2 | 0 | 0 | 0 | 480 | 0
29 | Wardha | PGCIL | Aurangabad-PG* | 1 | 348 | Hexa Zebra | 330 | Yes | 1x240+1x330 | 570 | 800 | 0 | 0 | 1 | 0
|  |  | Aurangabad-PG* | 2 | 348 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Aurangabad-PG* | 3 | 370 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Aurangabad-PG* | 4 | 370 | Hexa Zebra | 330 | Yes |  |  |  | 0 | 0 | 1 | 0
|  |  | Seoni | 1 | 261 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Seoni | 2 | 261 | Quad Bersimis | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Raipur-PS(Durg) | 1 | 370 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Raipur-PS(Durg) | 2 | 370 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Raipur-PS(Durg) | 3 | 361 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Raipur-PS(Durg) | 4 | 361 | Hexa Zebra | 330 | - |  |  |  | 0 | 0 | 0 | 1
|  |  | Nizamabad | 1 | 391 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  |  | Nizamabad | 2 | 391 | Hexa Zebra | 240 | - |  |  |  | 0 | 1 | 0 | 0
|  | Total MVAR |  |  |  |  | 3600 |  | 570 |  |  | 0 | 4 | 4 | 4 | 3600 | 0
* Charged at 400 kV
29160
7950

## 765kV BRs
Sr. No. | Name of S/S | Owner | Nos of Reactor | Total MVAR | Rated Voltage | 240 | 330
1 | Akola(2) | MEGPTCL | 3X80 | 240 | 800 | 1
2 | Aurangabad-PG | PGCIL | 3X80 | 240 | 800 | 1
3 | Bhopal-BDTCL | BDTCL | 3X80 | 240 | 800 | 1
4 | Bilaspur | PGCIL | 3X80 | 240 | 800 | 1
5 | Bina-NHPTL | NHPTL | - | - | -
6 | Bina-PG | PGCIL | 3X80 + 3X80 | 480 | 800 | 2
7 | Champa | PGCIL | 3X80 | 240 | 800 | 1
8 | Dharamjaygarh | PGCIL | 3X110 + 3X110 | 660 | 800 |  | 2
9 | Dhule-BDTCL | BDTCL | 3X80 | 240 | 800 | 1
10 | Ektuni (Aurangabad(3)) | MSETCL | 3X80 | 240 | 800 | 1
11 | Gadarwara | NTPC | - | - | -
12 | Gwalior | PGCIL | 3X80 | 240 | 800 | 1
13 | Indore-PG | PGCIL | 3X80 + 3X80 | 480 | 800 | 2
14 | Jabalpur-PS | PGCIL | 3X80 + 3X80 | 480 | 800 | 2
15 | Kholpaur-PG# | PGCIL | - | - | -
16 | Koradi(III) | MEGPTCL | 3X80 | 240 | 800 | 1
17 | Pune-PG(Shikrapur) | PGCIL | 3X80 | 240 | 800 | 1
18 | Raigarh-PS(Kotra) | PGCIL | 3X80 | 240 | 800 | 1
19 | Raipur-PS(Durg) | PGCIL | 3X80 | 240 | 800 | 1
20 | Sasan | SPL | 3X80 | 240 | 800 | 1
21 | Satna | PGCIL | 3X80 + 3X80 | 480 | 800 | 2
22 | Seoni | PGCIL | 3X80 | 240 | 800 | 1
23 | Sipat | NTPC | 3X80 | 240 | 800 | 1
24 | Solapur | PGCIL | 3X80 | 240 | 800 | 1 |  | 7950
25 | Tamnar | PGCIL | 3X80 | 240 | 800 | 1
26 | Tiroda | APML | 3X80 | 240 | 800 | 1
27 | Vadodora-PS | PGCIL | 3X80 | 240 | 800 | 1
28 | Vindhyachal-PS | PGCIL | 3X80 | 240 | 800 | 1
29 | Wardha | PGCIL | 3X80 + 3X110 | 570 | 800 | 1 | 1
|  | Total | 7950 | 7950 |  | 29 | 3

## 765 LR as BR
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Km | Conductor Type | SIL | No Load MVAR Generated | End1 LR |  | End2 LR |  | End 1 Over Voltage Stage 1 | End 1 Over Voltage Stage 2 | End 2 Over Voltage Stage 1 | End 2 Over Voltage Stage 2
[11 empty] | MVAR | S/W | MVAR | S/W
1 | Akola(2)* | Ektuni (Aurangabad(3)) | 2 | MEGPTCL | MEGPTCL | MSETCL | 219 | Quad Bersimis | 2194.4416 | 514.65 | 240 | Y | 240 | - | 108% - 5 Sec | 140% - 0.15 Sec | 108%-5Sec | 140%-0.1 Sec
2 | Akola(2)* | Ektuni (Aurangabad(3)) | 1 | MEGPTCL | MEGPTCL | MSETCL | 219 | Quad Bersimis | 2194.4416 | 514.65 | 240 | Y | 240 | - | 108 % - 7 Sec | 140 %- 0.15 Sec | 108%-8Sec | 140%-0.1 Sec
3 | Aurangabad-PG | Wardha* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 348 | Hexa Zebra | 2470.0035 | 925.68 | 240 | - | 330 | Y | 109 % -5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec
4 | Aurangabad-PG | Wardha* | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 348 | Hexa Zebra | 2470.0035 | 925.68 | 240 | - | 330 | Y | 109 % -7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec
5 | Aurangabad-PG | Wardha* | 3 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 240 | - | 330 | Y | 107 % -5 Sec | 150 %-0.1 Sec | 109 %-6 Sec | 150 %-0.1 Sec
6 | Aurangabad-PG | Wardha* | 4 | WRTS-1 | WRTS-1 | WRTS-1 | 370 | Hexa Zebra | 2470.0035 | 984.2 | 240 | - | 330 | Y | 107 % -6 Sec | 150 %-0.1 Sec | 109 %-8 Sec | 150 %-0.1 Sec
7 | Aurangabad-PG* | Solapur-PG* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 279 | Hexa Zebra | 2470.0035 | 742.14 | 240 | Y | 240 | Y | 108 % -7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec
8 | Aurangabad-PG* | Solapur-PG* | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 279 | Hexa Zebra | 2470.0035 | 742.14 | 240 | Y | 240 | Y | 108 % -8 Sec | 150 %-0.1 Sec | 109 %-8 Sec | 150 %-0.1 Sec
9 | Bhopal-BDTCL* | Indore-PG* | 1 | BDTCL | BDTCL | WRTS-2 | 176 | Quad Bersimis | 2194.4416 | 413.6 | 240 | Y | 240 | - | 108 % -5 Sec | 150 %-0.1 Sec | 108 % -5 Sec | 150 %-0.1 Sec
10 | Bilaspur* | Seoni | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 333 | Quad Bersimis | 2194.4416 | 782.55 | 240 | Y | 240 | - | 108 % -7 Sec | 150 %-0.1 Sec | 108 % -7 Sec | 150 %-0.1 Sec
11 | Bilaspur* | Seoni | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 335 | Quad Bersimis | 2194.4416 | 787.25 | 240 | Y | 240 | - | 110 % -5 Sec | 140 %-0.1 Sec | 107 % -5 Sec | 150 %-0.1 Sec
12 | Bilaspur* | Dharamjaygarh | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 89 | Quad Bersimis | 2194.4416 | 209.15 | 240 | Y | - | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec
13 | Bina-PG | Bina-NHPTL | 1 | WRTS-2 | WRTS-2 | NHPTL | 0.2 | Quad Bersimis | 2194.4416 | 0.47 | - | - | - | - | - | - | - | -
14 | Bina-PG* | Gwalior* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 235 | Quad Bersimis | 2194.4416 | 552.25 | 240 | - | 240 | Y | 108 %-7 Sec | 150 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec
15 | Bina-PG* | Gwalior* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 235 | Quad Bersimis | 2194.4416 | 552.25 | 240 | - | 240 | Y | 109%-8 Sec | 150 %-0.1 Sec | 109%-8 Sec | 150 %-0.1 Sec
16 | Bina-PG* | Gwalior* | 3 | WRTS-2 | WRTS-2 | WRTS-2 | 231 | Quad Bersimis | 2194.4416 | 542.85 | 240 | Y | 240 | Y | 109 %-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec
17 | Bina-PG* | Indore-PG* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 310 | Quad Bersimis | 2194.4416 | 728.5 | 240 | Y | 240 | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec
18 | Bina-PG* | Jabalpur-PS* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 230 | Quad Bersimis | 2194.4416 | 540.5 | 240 | - | 240 | Y | 107 %-5 Sec | 150 %-0.1 Sec | 107 %-5 Sec | 150 %-0.1 Sec
19 | Bina-PG* | Jabalpur-PS* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 230 | Quad Bersimis | 2194.4416 | 540.5 | 240 | - | 240 | Y | 108 %- 7 Sec | 150 %-0.1 Sec | 108 %- 7 Sec | 150 %-0.1 Sec
20 | Bina-PG* | Jabalpur-PS* | 3 | JTCL | WRTS-2 | WRTS-2 | 236 | Quad Bersimis | 2194.4416 | 554.6 | 240 | - | 240 | Y | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150%-0.1 Sec
21 | Champa | Dharamjaygarh | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 56 | Quad Bersimis | 2194.4416 | 131.6 | - | - | - | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150%-0.1 Sec
22 | Dharamjaygarh | Ranchi | 1 | ERTS-1/WRTS-1 | WRTS-1 | ERTS-1 | 303 | Quad Bersimis | 2194.4416 | 712.05 | 330 | - | 240 | Y | 107 % -5 Sec | 150 %-0.1 Sec | 107 % -5 Sec | 150 %-0.1 Sec
23 | Dharamjaygarh | Ranchi | 2 | ERTS-1/WRTS-1 | WRTS-1 | ERTS-1 | 354 | Quad Bersimis | 2194.4416 | 831.9 | 330 | - | 240 | Y | 108 %-7 Sec | 150 %-0.1 Sec | 107 %-5 Sec | 150 %-0.1 Sec
24 | Dharamjaygarh* | Jharsuguda | 1 | WRTS-1 | WRTS-1 | ERTS-2 | 151 | Hexa Zebra | 2470.0035 | 401.66 | 330 | Y | - | - | 108 %-7 Sec | 150%-0.1 Sec | 108 %-6 Sec | 150%-0.1 Sec
25 | Dharamjaygarh* | Jharsuguda | 2 | WRTS-1 | WRTS-1 | ERTS-2 | 151 | Hexa Zebra | 2470.0035 | 401.66 | 330 | Y | - | - | 107 %-5 Sec | 150%-0.1 Sec | 108%-5 Sec | 150%-0.1 Sec
26 | Dharamjaygarh* | Jabalpur-PS* | 1 | WRTS-1 | WRTS-1 | WRTS-2 | 424 | Hexa Zebra | 2470.0035 | 1127.84 | 330 | Y | 240 | - | 108 %-5 Sec | 150%-0.1 Sec | 108 %- 5 Sec | 150%-0.1 Sec
27 | Dharamjaygarh* | Jabalpur-PS* | 2 | WRTS-1 | WRTS-1 | WRTS-2 | 424 | Hexa Zebra | 2470.0035 | 1127.84 | 330 | Y | 240 | - | 108 %-7 Sec | 150%-0.1 Sec | 107 %- 7 Sec | 150%-0.1 Sec
28 | Dharamjaygarh* | Jabalpur-PS* | 3 | JTCL | WRTS-1 | WRTS-2 | 379 | Hexa Zebra | 2470.0035 | 1008.14 | 330 | Y | 240 | - | 107 %-5 Sec | 150%-0.1 Sec | 108 %- 6 Sec | 150 %-0.1 Sec
29 | Dharamjaygarh* | Jabalpur-PS* | 4 | JTCL | WRTS-1 | WRTS-2 | 379 | Hexa Zebra | 2470.0035 | 1008.14 | 330 | Y | 240 | - | 107 %-7 Sec | 150%-0.1 Sec | 107 %- 8 Sec | 150 %-0.1 Sec
30 | Dharamjaygarh*^ | Jharsuguda^ | 3 | WRTS-1 | WRTS-1 | ERTS-2 | 303 | Hexa Zebra | 2470.0035 | 805.98 | 330 | Y | - | - | - | - | ERLDC | ERLDC
31 | Dharamjaygarh*^ | Jharsuguda^ | 4 | WRTS-1 | WRTS-1 | ERTS-2 | 303 | Hexa Zebra | 2470.0035 | 805.98 | 330 | Y | - | - | - | - | ERLDC | ERLDC
32 | Dhule-BDTCL* | Aurangabad-PG | 1 | BDTCL | BDTCL | WRTS-I | 192 | Quad Bersimis | 2194.4416 | 451.2 | 240 | Y | - | - | 108 %-5 Sec | 150%-0.1 Sec | 108 %- 6 Sec | 150 %-0.1 Sec
33 | Gwalior | Agra | 1 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 129 | Quad Bersimis | 2194.4416 | 303.15 | - | - | - | - | 108 %-5 Sec | 150%-0.1 Sec | NRLDC | NRLDC
34 | Gwalior | Agra | 2 | NRTS-1/WRTS-2 | WRTS-2 | NRTS-1 | 128 | Quad Bersimis | 2194.4416 | 300.8 | - | - | - | - | 109 %-7 Sec | 150%-0.1 Sec | NRLDC | NRLDC
35 | Gwalior* | Jaipur | 1 | NRTS-1/WRTS-2 | WRTS-2 | RRVPNL | 304 | Quad Bersimis | 2194.4416 | 714.4 | 240 | Y | 240 | - | 108 %-5 Sec | 150 %-0.1 Sec | NRLDC | NRLDC
36 | Gwalior* | Jaipur | 2 | NRTS-1/WRTS-2 | WRTS-2 | RRVPNL | 311 | Quad Bersimis | 2194.4416 | 730.85 | 240 | Y | 240 | - | 107 %-4 Sec | 150 %-0.1 Sec | NRLDC | NRLDC
37 | Jabalpur (PS) | Gadarwara | 1 | WRTS-2 | WRTS-2 | NTPC | 102 | Hexa Zebra | 2470.0035 | 271.32 | - | - | - | - | 107%, 5 sec | 150 %-0.1 Sec | - | -
38 | Jabalpur (PS) | Gadarwara | 2 | WRTS-2 | WRTS-2 | NTPC | 102 | Hexa Zebra | 2470.0035 | 271.32 | - | - | - | - | 108%, 7 sec | 150 %-0.1 Sec | - | -
39 | Jabalpur-PS* | Bhopal-BDTCL* | 1 | BDTCL | WRTS-2 | BDTCL | 260 | Quad Bersimis | 2194.4416 | 611 | 240 | Y | 240 | Y | 108 %-5 Sec | 150 %-0.1 Sec | 110 %-5 Sec | 150 %-0.1 Sec
40 | Jabalpur-PS^ | Orai^ | 1 | WRTS-2/NRTS-2 | WRTS-2 | NRTS-2 | 360 | Hexa Zebra | 2470.0035 | 957.6 | 330 | - | - | - | - | - | NRLDC | NRLDC
41 | Jabalpur-PS^ | Orai^ | 2 | WRTS-2/NRTS-2 | WRTS-2 | NRTS-2 | 360 | Hexa Zebra | 2470.0035 | 957.6 | 330 | - | - | - | - | - | NRLDC | NRLDC
42 | Kholpaur-PG# | Kudgi# | 1 | WRTS-1 | WRTS-1 | SRTS-1 | 191 | Hexa Zebra | 2470.0035 | 508.06 | - | - | - | - | 110 %-5 Sec | 150 %-0.1 Sec | 110 %-5 Sec | 150 %-0.1 Sec
43 | Kholpaur-PG# | Kudgi# | 2 | WRTS-1 | WRTS-1 | SRTS-1 | 191 | Hexa Zebra | 2470.0035 | 508.06 | - | - | - | - | 110 %-7 Sec | 150 %-0.1 Sec | 110 %-7 Sec | 150 %-0.1 Sec
44 | Koradi(III) | Akola(2)* | 1 | MEGPTCL | MEGPTCL | MEGPTCL | 222 | Quad Bersimis | 2194.4416 | 521.7 | 240 | Y | 240 | Y | 110 %-7 Sec | 140 %-0.15 Sec | 110% - 7 Sec | 140% - 0.15Sec
45 | Koradi(III) | Akola(2)* | 2 | MEGPTCL | MEGPTCL | MEGPTCL | 222 | Quad Bersimis | 2194.4416 | 521.7 | 240 | Y | 240 | Y | 110 %-5 Sec | 140 %-0.15 Sec | 110% - 5 Sec | 140% - 0.15Sec
46 | Pune-PG (Shikrapur)* | Solapur-PG* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 270 | Quad Bersimis | 2194.4416 | 634.5 | 240 | Y | 240 | Y | 110 %-7 Sec | 140 %-0.15 Sec | 110 %-7 Sec | 140 %-0.15 Sec
47 | Raigarh-PS(Kotra) | Raipur-PS(Durg) | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 235 | Hexa Zebra | 2470.0035 | 625.1 | 240 | Y | 240 | - | 110 %-5 Sec | 140 %-0.15 Sec | 110 %-5 Sec | 140 %-0.15 Sec
48 | Raigarh-PS(Kotra) | Tamnar | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 48 | Hexa Zebra | 2470.0035 | 127.68 | - | - | - | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec
49 | Raigarh-PS(Kotra) | Tamnar | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 48 | Hexa Zebra | 2470.0035 | 127.68 | - | - | - | - | 107 %-7 Sec | 150 %-0.1 Sec | 107 %-7 Sec | 150 %-0.1 Sec
50 | Raigarh-PS(Kotra) | Champa | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 96 | Quad Bersimis | 2194.4416 | 225.6 | - | - | - | - | 108 %-5Sec | 150 %-0.1 Sec | 110 %-5Sec | 150 %-0.1 Sec
51 | Raigarh-PS(Kotra)* | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 235 | Hexa Zebra | 2470.0035 | 625.1 | 240 | Y | 240 | - | 107 % -5 Sec | 150 %-0.1 Sec | 107 % -5 Sec | 150 %-0.1 Sec
52 | Raipur-PS(Durg) | Champa | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 153 | Hexa Zebra | 2470.0035 | 406.98 | 240 | - | - | - | 109 %-6 Sec | 150 %-0.1 Sec | 110 %-5 Sec | 150 %-0.1 Sec
53 | Raipur-PS(Durg) | Champa | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 150 | Hexa Zebra | 2470.0035 | 399 | 240 | - | - | - | 109 %-6 Sec | 150 %-0.1 Sec | 110 %-6 Sec | 150 %-0.1 Sec
54 | Sasan | Satna* | 1 | WRTS-2 | SPL | WRTS-2 | 246 | Quad Bersimis | 2194.4416 | 578.1 | 240 | Y | 240 | - | 108 %-5Sec | 150 %-0.1 Sec | 109%-5 sec | 150 %-0.1 Sec
55 | Sasan | Satna* | 2 | WRTS-2 | SPL | WRTS-2 | 243 | Quad Bersimis | 2194.4416 | 571.05 | 240 | Y | 240 | - | 108 %-5 Sec | 150 %-0.1 Sec | 108%-7 sec | 150 %-0.1 Sec
56 | Sasan | Vindhyachal-PS | 1 | WRTS-2 | SPL | WRTS-2 | 6 | Quad Bersimis | 2194.4416 | 14.1 | - | - | - | - | 110 %-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec
57 | Satna* | Gwalior* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 337 | Quad Bersimis | 2194.4416 | 791.95 | 240 | Y | 240 | - | 109%-5 sec | 150 %-0.1 Sec | 109%-5 sec | 150 %-0.1 Sec
58 | Satna* | Gwalior* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 337 | Quad Bersimis | 2194.4416 | 791.95 | 240 | Y | 240 | - | 109%-6 sec | 150 %-0.1 Sec | 109%-6 sec | 150 %-0.1 Sec
59 | Satna* | Bina-PG* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 274 | Quad Bersimis | 2194.4416 | 643.9 | 240 | Y | 240 | - | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec
60 | Satna* | Bina-PG* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 276 | Quad Bersimis | 2194.4416 | 648.6 | 240 | Y | 240 | - | 109 %-7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec
61 | Satna* | Vindhyachal-PS* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 237 | Quad Bersimis | 2194.4416 | 556.95 | 240 | - | 240 | Y | 108 %-5 Sec | 150 %-0.1 Sec | 108 %-5 Sec | 150 %-0.1 Sec
62 | Satna* | Vindhyachal-PS* | 2 | WRTS-2 | WRTS-2 | WRTS-2 | 237 | Quad Bersimis | 2194.4416 | 556.95 | 240 | - | 240 | Y | 109 %-7 Sec | 150 %-0.1 Sec | 109 %-7 Sec | 150 %-0.1 Sec
63 | Seoni* | Bina-PG* | 1 | WRTS-1 | WRTS-1 | WRTS-2 | 292 | Quad Bersimis | 2194.4416 | 686.2 | 240 | Y | 240 | - | 108 % -7 Sec | 150 %-0.1 Sec | 108 % -7 Sec | 150 %-0.1 Sec
64 | Seoni* | Wardha | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 261 | Quad Bersimis | 2194.4416 | 613.35 | 240 | Y | 240 | - | 109 %- 7 Sec | 150 %-0.1 Sec | 109 %- 7 Sec | 150 %-0.1 Sec
65 | Seoni* | Wardha | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 261 | Quad Bersimis | 2194.4416 | 613.35 | 240 | Y | 240 | - | 108 %-7 Sec | 150 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec
66 | Sipat | Bilaspur | 1 | WRTS-1 | NTPC | WRTS-1 | 22 | Quad Bersimis | 2194.4416 | 51.7 | 240 | Y | - | - | 109%-5 Sec | 150 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec
67 | Sipat | Bilaspur | 2 | WRTS-1 | NTPC | WRTS-1 | 22 | Quad Bersimis | 2194.4416 | 51.7 | 240 | Y | - | - | 108 %-6 Sec | 150 %-0.1 Sec | 108 %-6 Sec | 150 %-0.1 Sec
68 | Solapur* | Raichur | 1 | RSTCL | WRTS-1 | SRTS-1 | 208 | Quad Bersimis | 2194.4416 | 488.8 | 240 | Y | 240 | Y | 110 %-4 Sec | 140 %-0.1 Sec | 109 %-5 Sec | 150 %-0.1 Sec
69 | Solapur* | Raichur | 2 | RSTCL | WRTS-1 | SRTS-1 | 208 | Quad Bersimis | 2194.4416 | 488.8 | 240 | Y | 240 | Y | 110 %-4 Sec | 140 %-0.1 Sec | 108 %-7 Sec | 150 %-0.1 Sec
70 | Tiroda* | Koradi(III) | 1 | MEGPTCL | APML | MEGPTCL | 136 | Quad Bersimis | 2194.4416 | 319.6 | 240 | Y | 240 | Y | 110 %-5 Sec | 140 %-0.15 Sec | 110 %-5 Sec | 140 %-0.15 Sec
71 | Tiroda* | Koradi(III) | 2 | MEGPTCL | APML | MEGPTCL | 138 | Quad Bersimis | 2194.4416 | 324.3 | 240 | Y | 240 | Y | 110 %-7 Sec | 140 %-0.15 Sec | 110 %-7 Sec | 140 %-0.15 Sec
72 | Vadodora-PS | Indore-PG* | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 293 | Quad Bersimis | 2194.4416 | 688.55 | 240 | - | 240 | Y | 109%, 6sec | 150%, 0.1 sec | 109%, 6sec | 150%, 0.1 sec
73 | Vadodora-PS | Dhule-BDTCL* | 1 | BDTCL | WRTS-2 | BDTCL | 268 | Quad Bersimis | 2194.4416 | 629.8 | 240 | - | 240 | Y | 108 %-5 Sec | 140 %-0.15 Sec | 108%-5 sec | 140 %-0.15 Sec
74 | Wardha | Raipur-PS(Durg)* | 1 | WRTS-1 | WRTS-1 | WRTS-1 | 377 | Hexa Zebra | 2470.0035 | 1002.82 | 330 | - | 240 | Y | 107 %-5 Sec | 150 %-0.1 Sec | 107 %-5 Sec | 150 %-0.15Sec
75 | Wardha | Raipur-PS(Durg) | 2 | WRTS-1 | WRTS-1 | WRTS-1 | 377 | Hexa Zebra | 2470.0035 | 1002.82 | 330 | - | 240 | Y | 107 %-7 Sec | 150 %-0.1 Sec | 107 %-7Sec | 150 %-0.15Sec
76 | Wardha | Raipur-PS(Durg)* | 3 | WRTS-1 | WRTS-1 | WRTS-1 | 361 | Hexa Zebra | 2470.0035 | 960.26 | 330 | - | 240 | Y | 107 %-6 Sec | 150 %-0.1 Sec | 107 %-6Sec | 150 %-0.15Sec
77 | Wardha | Raipur-PS(Durg)* | 4 | WRTS-1 | WRTS-1 | WRTS-1 | 361 | Hexa Zebra | 2470.0035 | 960.26 | 330 | - | 240 | Y | 107 %-8 Sec | 150 %-0.1 Sec | 107 %-8Sec | 150 %-0.15Sec
78 | Wardha* | Nizamabad | 1 | WRTS-1/ SRTS-1 | WRTS-1 | SRTS-1 | 291 | Hexa Zebra | 2470.0035 | 774.06 | 240 | Y | 240 | Y | 108 %-5 Sec | 150 %-0.1 Sec | 111 %-10 Sec | 150%- 0.1 sec
79 | Wardha* | Nizamabad | 2 | WRTS-1/ SRTS-1 | WRTS-1 | SRTS-1 | 291 | Hexa Zebra | 2470.0035 | 774.06 | 240 | Y | 240 | Y | 109 %-7 Sec | 150 %-0.1 Sec | 110 %-7 Sec | 150%-0.1 sec
# 765 kV line charged at 400 kV, * Can be converted as BR by Bypassing NGR Manually | [6 empty] | 18968.2 |  |  |  | 17520 | Total | 13560

## 1200 kV SS Res
Sr. No. | Name of S/S | S/S Owner | Lines | ID | km | Conductor Type | LRs | LRs S/W | BRs
1 | Bina-NTS | PGCIL | 1 | 1 | 1.9 | Octa Bersimis | - | - | -

## 400kV SS and BRs
S.no | Substation | State | S/S Owner | Owner | Nos of Reactor | Total MVAR | Rated Voltage | 50x35+40x125+17x63+27x80
1 | ACBIL | [6 empty] | 9981
2 | Akola
3 | Akola(2)
4 | Alkud |  |  | MSETCL | 1X125 | 125 | 420
5 | Amreli |  |  | GETCO | 1X50 + 1X125 | 175 | 420
6 | APL-Mundra |  |  | APL | 2X80 + 1X125 | 285 | 420
7 | Asoj |  |  | GETCO | 1X50 | 50 | 420
8 | Astha |  |  | MPPTCL | 1x50 | 50 | 420
9 | Athena |  |  | ACPL
10 | Aurangabad-M(Waluj)
11 | Aurangabad-PG |  |  | PGCIL | 1X125 | 125 | 420
12 | Bableshwar |  |  | MSETCL | 2X80 | 160 | 420
13 | Bachau |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
14 | Balco
15 | Betul |  |  | PGCIL | 1x125 | 125 | 420
16 | Bhadrawati |  |  | PGCIL | 1X50 | 50 | 420
17 | Bhatapara |  |  | PGCIL | 1X125 | 125 | 420
18 | Bhilai
19 | Bhopal-BDTCL |  |  | BDTCL | 1X125 | 125 | 420
20 | Bhopal-MP |  |  | MPPTCL | 1X125 + 1x80 | 205 | 420
21 | Bhusawal (Khadka) |  |  | MSETCL | 1X50 | 50 | 420
22 | Bilaspur
23 | Bina-MP |  |  | MPPTCL | 1X50 | 50 | 420
24 | Bina-NHPTL |  |  | NHPTL
25 | Bina-NTS |  |  | PGCIL
26 | Bina-PG |  |  | PGCIL | 1X125 | 125 | 420
27 | Birsingpur |  |  | MPPGCL | 1X50 | 50 | 420
28 | Boisar
29 | CGPL |  |  | CGPL | 1x63 | 63 | 420
30 | Chakan
31 | Champa |  |  | PGCIL | 1x80 | 80 | 420
32 | Chandrapur
33 | Chandrapur-GCR
34 | Chandrapur-II
35 | Charnaka |  |  | GETCO | 1x125 | 125
36 | Chhegaon |  |  | MPPTCL | 1x50 | 50 | 420
37 | Chorania |  |  | GETCO | 1X50 + 1X125 | 175 | 420
38 | Damoh |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
39 | DB-Power
40 | Deepnagar
41 | Dehgam |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
42 | DGEN |  |  | DGEN | 1X125 | 125 | 420
43 | Dhariwal |  |  | DIL | 1x80 | 80 | 420
44 | Dhariwal-MS
45 | Dhule-BDTCL
46 | Dhule-MS |  |  | MSETCL | 1X80 | 80 | 420
47 | Ektuni (Aurangabad(3)) |  |  | MSETCL
48 | EMCO |  |  | GMR | 1X80 | 80 | 420
49 | Essar_Mahan |  |  | ESSAR | 1X80 | 80 | 420
50 | Gandhar |  |  | NTPC | 1X50 | 50 | 420
51 | GMR-CG |  |  | GMR | 1x125 | 125 | 420
52 | GPEC |  |  | GSECL
53 | Gwalior |  |  | PGCIL | 3X125 | 375 | 420
54 | Hadala |  |  | GETCO | 1X50 + 1X125 | 175 | 420
55 | Hazira
56 | IEPL
57 | Indira Sagar
58 | Indore-MP
59 | Indore-PG |  |  | PGCIL | 1X125 + 1X63 | 188 | 420
60 | Itarsi |  |  | PGCIL | 2X125 + 1X50 | 300 | 420
61 | Jabalpur |  |  | PGCIL | 1X125 + 1X63 | 188 | 420
62 | Jabalpur (PS) |  |  | PGCIL | 2X125 | 250 | 420
63 | Jagdalpur |  |  | CSPTCL | 1x80 | 80 | 420
64 | Jaigad |  |  | JPTL | 2x50 | 100 | 420
65 | Jejuri
66 | Jetpur |  |  | GETCO | 1X50 + 1X63 | 113 | 420
67 | Jhabua Power |  |  |  | 1x125 | 125 | 420
68 | JP-Bina
69 | JPL |  |  | JPL | 1x125 | 125 | 420
70 | JPL_extn(Tamnar)
71 | JP-Nigrie |  |  | JPVL | 1X125 | 125 | 420
72 | Julwania |  |  | MPPTCL | 1x50 | 50 | 420
73 | Kala |  |  | PGCIL | 1X80 | 80 | 420
74 | Kalwa
75 | Karad |  |  | MSETCL | 1X80 | 80 | 420
76 | Kasor |  |  | GETCO | 1X50 + 1X125 | 175 | 420
77 | Katni
78 | Khandwa |  |  | PGCIL | 2X125 | 250 | 420
79 | Khaparkheda
80 | Kharghar |  |  | MSETCL | 1X80 | 80 | 420
81 | Kolhapur |  |  | MSETCL | 1X80 | 80 | 420
82 | Kolhapur-PG |  |  | PGCIL | 1x125 | 125 | 420
83 | Koradi |  |  | MSETCL | 1X50 | 50 | 420
84 | Koradi-II
85 | Korba (W)
86 | Korba (W)-Ext
87 | Korba-NTPC
88 | Kosamba |  |  | GETCO | 1X80 | 80 | 420
89 | Koyna stage-IV
90 | KSK Mahanadi
91 | KWPCL
92 | Lara |  |  | NTPC
93 | Lonikhand |  |  | MSETCL | 1X50 | 50 | 420
94 | Lonikhand-II
95 | Magarawada |  |  | PGCIL | 1x80 | 80 | 420
96 | Malwa
97 | Mansar |  |  | GETCO | 1x63 | 63 | 420
98 | Mapusa |  |  | PGCIL | 1X50 | 50 | 420
99 | Marwa
100 | MB Power |  |  | MB Power | 1x125 | 125 | 420
101 | MCCPL
102 | Mouda |  |  | NTPC | 2x80 | 160 | 420
103 | Nagda |  |  | MPPTCL | 2X50 | 100 | 420
104 | Nagothane |  |  | MSETCL | 1X80 | 80 | 420
105 | Nanded |  |  | MSETCL
106 | Nandgaonpeth |  |  | Rattan India | 1x80 | 80 | 420
107 | Navsari |  |  | PGCIL | 1X63 | 63 | 420
108 | New koyna
109 | Nicol-II
110 | NSPCL
111 | Padghe |  |  | MSETCL | 1X80 | 80 | 420
112 | Parli-M |  |  | MSETCL | 1X50 | 50 | 420
113 | Parli-PG |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
114 | Pathadi
115 | Pirana-PG |  |  | PGCIL | 1X125 | 125 | 420
116 | Pirana-T
117 | Pithampur |  |  | MPPTCL | 1x50 | 50 | 420
118 | Pune-PG |  |  | PGCIL | 1X50 | 50 | 420
119 | Pune-PG(Shikrapur)
120 | Raigarh |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
121 | Raigarh-PS(Kotra) |  |  | PGCIL | 1X80 | 80 | 420
122 | Raipur |  |  | PGCIL | 1X125 + 1X80 | 205 | 420
123 | Raipur-PS(Durg)
124 | Raita
125 | Rajgarh |  |  | PGCIL | 1X125 | 125 | 420
126 | Ranchodpura |  |  | GETCO | 1X50 + 1X125 | 175 | 420
127 | RGPPL
128 | RKM |  |  | RKM | 2x50 | 100 | 420
129 | Sami |  |  | APL | 1X50 | 50 | 420
130 | Sasan
131 | Satna |  |  | PGCIL | 1X50 + 1X63 | 113 | 420
132 | Satpura |  |  | MPPTCL | 2X63 | 126 | 420
133 | Seoni |  |  | PGCIL | 2x125 | 250 | 420
134 | Sholapur-M
135 | Shujalpur |  |  | PGCIL | 1X63 + 1X125 | 188 | 420
136 | Sipat
137 | SKS |  |  | SPGCL | 1x50 | 50 | 420
138 | Soja |  |  | GETCO | 1X50 + 1X80 | 130 | 420
139 | Solapur-NTPC |  |  | NTPC | 1x80 | 80 | 420
140 | Solapur-PG |  |  | PGCIL | 1X63 | 63 | 420
141 | SSP
142 | Sugen
143 | Tamnar-PS
144 | Taptithanda
145 | Tarapur-3&4
146 | Tiroda |  |  | APML | 2X80 | 160 | 420
147 | TRN
148 | Ukai
149 | Uno-Sugen |  |  | TPL | 1x80 | 80 | 420
150 | Vadinar
151 | Vadodara-PS
152 | Vandana
153 | Vapi
154 | Varsana |  |  | GETCO | 1X50 + 1X125 | 175 | 420
155 | Veloda |  |  | GETCO | 1x125 | 125 | 420
156 | Vindhyachal |  |  | NTPC | 1X63 + 1X50 | 113 | 420
157 | Vindhyachal-III
158 | Vindhyachal-IV |  |  | NTPC | 1X80 | 80 | 420
159 | Vindhyachal-PS |  |  | PGCIL | 1X63 | 63 | 420
160 | Vindhyachal-V |  |  | NTPC | 1x125 | 125 | 420
161 | Wanakbori
162 | Wardha |  |  | PGCIL | 1X50 | 50 | 420
163 | Warora |  |  | ATIL | 1x125 | 125 | 420
164 | Zerda(Kansari) |  |  | GETCO | 1X50 + 1x125 | 175 | 420

## 400 kV SS Res
Sr. No. | Name of S/S | S/S Owner | Lines | ID | Line Length (in km) | Conductor Type | LRs | LRs S/W | BRs | Line Owner | End-2 Owner |  | 50 MVAR SLRs | 50 MVAR NSLRs | 63 MVAR SLRs | 63 MVAR NSLRs | 80 MVAR SLRs | 80 MVAR NSLRs
1 | ACBIL | ACBIL | Bilaspur | 1 | 56 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MCCPL | 1 | 16 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 |  | Formula Change
2 | Akola | MSETCL | Aurangabad-PG | 1 | 178 | Twin ACSR Moose | 50 | - | - |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
|  |  | Aurangabad-PG | 2 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5
|  |  | Nandgaonpeth | 1 | 117 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Akola(2) | 1 | 30 | Quad ACSR Moose | - | - |  |  |  | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Akola(2) | 2 | 30 | Quad ACSR Moose | - | - |  |  |  | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Bhusawal (Khadka) | 1 | 182 | Twin ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Wardha | 1 | 162 | Twin ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  |  | Wardha | 2 | 162 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
|  | Total |  |  |  |  | 100 | [5 empty] | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 14 | Formula Change
3 | Akola(2) | MSETCL | Nandgaonpeth | 1 | 104 | Twin ACSR Moose | - | - | - |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  |  | Nandgaonpeth | 2 | 104 | Twin ACSR Moose | - | - |  |  |  | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  |  | Akola | 1 | 30 | Quad ACSR Moose | - | - |  |  |  | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  |  | Akola | 2 | 30 | Quad ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14
|  | Total |  |  |  |  | - | [5 empty] | 0 | 2 | 0 | 0 | 0 | 0 | 17 | 19
4 | Alkud | MSETCL | Solapur-PG | 1 | 12 | Twin ACSR Moose |  |  | 125 | WRTMPL |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19
|  |  | Kolhapur | 1 | 12 | Twin ACSR Moose |  |  |  | WRTMPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19
|  | Total | [6 empty] | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | Formula Change
5 | Amreli | GETCO | Hadala | 1 | 165 | Twin ACSR Moose | - | - | 1X50 + 1X125 |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22
|  |  | Chorania | 1 | 164 | Twin ACSR Moose | - | - |  |  |  | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22
|  |  | Jetpur | 1 | 96 | Twin ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22
|  |  | Jetpur | 2 | 96 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22
|  | Total |  |  |  |  | - | - | 175 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
6 | APL-Mundra | APL | Sami | 1 | 282 | Twin ACSR Moose | - | - | 2X80 + 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
|  |  | Sami | 2 | 282 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
|  |  | Hadala | 1 | 233 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
|  |  | Varsana | 1 | 84 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
|  |  | Varsana | 2 | 84 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
|  |  | Zerda(Kansari) | 1 | 332 | Twin ACSR Moose | - | - |  |  |  | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27
|  | Total |  |  |  |  | - |  | 285 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34
7 | Asoj | GETCO | Chorania | 1 | 177 | Twin ACSR Moose | - | - | 1X50 |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | Chorania | 2 | 166 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | Kosamba | 1 | 122 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | Wanakbori | 1 | 76 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | Indore-MP | 1 | 289 | Twin ACSR Moose | 50 | - |  |  |  | 125 | 0 | 1 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | Indore-MP | 2 | 273 | Twin ACSR Moose | 50 | - |  |  |  | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | SSP | 1 | 83 | Twin ACSR Moose | - | - |  |  |  | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | Vadodara-PS | 1 | 14 | Quad ACSR Moose | - | - |  |  |  | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34
|  |  | Vadodara-PS | 2 | 14 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34
|  | Total |  |  |  |  | 150 |  | 50 |  |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 42 | 44
8 | Astha | MPPTCL | Satpura | 1 | 240 | Twin ACSR Moose | - | - | 50 |  |  | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 44
|  |  | Satpura | 2 | 240 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 44
|  | Total |  |  |  |  | - |  | 50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
9 | Athena | ACPL | Raigarh-PS(Kotra) | 1 | 25 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
|  |  | Raigarh-PS(Kotra) | 2 | 25 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 47
|  | Total |  |  |  |  | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 50
10 | Aurangabad-M(Waluj) | MSETCL | Pune-PG(Shikrapur) | 1 | 315 | Twin ACSR Moose | 50 | - | - |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 48 | 50
|  |  | Pune-PG(Shikrapur) | 2 | 315 | Twin ACSR Moose | 50 | - |  |  |  | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 48 | 50
|  |  | Aurangabad-PG | 1 | 54 | Quad ACSR Moose | - | - |  |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 50
|  |  | Aurangabad-PG | 2 | 54 | Quad ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 50
|  |  | Taptithanda | 1 | 135 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 50
|  |  | Deepnagar | 2 | 185 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 50
|  |  | Bableshwar | 1 | 131 | Twin ACSR Moose | - | - |  |  |  | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 50
|  |  | Bhusawal (Khadka) | 1 | 238 | Twin ACSR Moose | 50 | - |  |  |  | 175 | 0 | 1 | 0 | 0 | 0 | 0 | 48 | 50
|  | Total |  |  |  |  | 150 |  | - |  |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 57 | 59
11 | Aurangabad-PG | PGCIL | Boisar | 1 | 327 | Twin ACSR Moose | 80 | Yes | 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 57 | 59
|  |  | Boisar | 2 | 327 | Twin ACSR Moose | 80 | Yes |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 57 | 59
|  |  | Akola | 1 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 57 | 59
|  |  | Akola | 2 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 188 | 0 | 1 | 0 | 0 | 0 | 0 | 57 | 59
|  |  | Aurangabad-M(Waluj) | 1 | 54 | Quad ACSR Moose | - | - |  |  |  | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 59
|  |  | Aurangabad-M(Waluj) | 2 | 54 | Quad ACSR Moose | - | - |  |  |  | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 59
|  | Total |  |  |  |  | 260 | - | 125 |  |  |  | 0 | 2 | 0 | 0 | 2 | 0 | 64 | 66
12 | Bableshwar | MSETCL | Padghe | 1 | 174 | Twin ACSR Moose | - | - | 2X80 |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | Padghe | 2 | 174 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | Aurangabad-M(Waluj) | 1 | 131 | Twin ACSR Moose | - | - |  |  |  | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | IB-Nasik | 1 | 72 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | IB-Nasik | 2 | 72 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | Bhusawal (Khadka) | 1 | 220 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | Dhule | 1 | 170 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | Dhule | 2 | 170 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | Ektuni (Aurangabad(3)) | 1 | 127 | Quad ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  |  | Ektuni (Aurangabad(3)) | 2 | 127 | Quad ACSR Moose | - | - |  |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 66
|  | Total |  |  |  |  | - |  | 160 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
13 | Bachau | PGCIL | Ranchodpura | 1 | 282 | Triple ACSR Snowbird | - | - | 1X63 + 1X125 |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | Ranchodpura | 2 | 282 | Triple ACSR Snowbird | - | - |  |  |  | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | Varsana | 1 | 10 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | Varsana | 2 | 10 | Twin ACSR Moose | - | - |  |  |  | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | CGPL | 1 | 100 | Triple ACSR Snowbird | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | CGPL | 2 | 100 | Triple ACSR Snowbird | - | - |  |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | Chorania | 1 | 220 | Triple ACSR Snowbird | - | - |  | WRTS-2 | GETCO | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | Mansar | 1 | 128 | Triple ACSR Snowbird | - | - |  | WRTS-2 | GETCO | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | CGPL | 3 | 122 | Triple ACSR Snowbird | - | - |  | WRTS-2 | CGPL | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | CGPL | 4 | 122 | Triple ACSR Snowbird | - | - |  | WRTS-2 | CGPL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 77
|  |  | Vadinar | 1 | 226 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 75 | 77
|  |  | Vadinar | 2 | 226 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 75 | 77
|  | Total |  |  |  |  | 126 |  | 188 |  |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 88 | 90
14 | Balco | Balco | Dharamjaygarh | 1 | 23.2 | Twin ACSR Moose | - | - | - |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 90
|  |  | Dharamjaygarh | 2 | 23.2 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 90
|  | Total |  |  |  |  | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 93
15 | Betul | PGCIL | Khandwa | 1 | 169 | Quad ACSR Moose | 50 | Yes | 1x125 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 91 | 93
|  |  | Khandwa | 2 | 169 | Quad ACSR Moose | 50 | Yes |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 91 | 93
|  |  | Mouda* | 1 | 193 | Quad ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 93
|  |  | Mouda* | 2 | 193 | Quad ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 93
|  | Total |  |  |  |  | 100 |  | 125 |  |  |  | 2 | 0 | 0 | 0 | 0 | 0 | 96 | 98
16 | Bhadrawati | PGCIL | Bhilai | 1 | 322 | Twin ACSR Moose | 50 | - | 1X50 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Raipur | 1 | 333 | Twin ACSR Moose | 50 | - |  |  |  | 63 | 0 | 1 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Raipur | 2 | 346 | Twin ACSR Moose | 63 | - |  |  |  | 50 | 0 | 0 | 0 | 1 | 0 | 0 | 96 | 98
|  |  | Raipur | 3 | 346 | Twin ACSR Moose | 63 | - |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 96 | 98
|  |  | EMCO | 1 | 28 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | EMCO | 2 | 28 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Parli-PG | 1 | 388 | Twin ACSR Moose | 63 | - |  |  |  | 160 | 0 | 0 | 0 | 1 | 0 | 0 | 96 | 98
|  |  | Dhariwal | 1 | 15 | Twin ACSR Moose | 63 | - |  |  |  | 100 | 0 | 0 | 0 | 1 | 0 | 0 | 96 | 98
|  |  | Ramagundam | 1 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Ramagundam | 2 | 178 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Chandrapur | 1 | 20 | Twin ACSR Moose | - | - |  |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Chandrapur | 2 | 20 | Twin ACSR Moose | - | - |  |  |  | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Chandrapur | 3 | 22 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 98
|  |  | Chandrapur | 4 | 22 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 98
|  | Total |  |  |  |  | 452 |  | 50 |  |  |  | 0 | 4 | 0 | 4 | 0 | 0 | 111 | 113
17 | Bhatapara | PGCIL | Bhilai | 1 | 93 | Twin ACSR Moose | 50 | - | 1X125 |  |  | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 111 | 113
|  |  | Korba-NTPC | 1 | 124 | Twin ACSR Moose | - | - |  |  |  | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 113
|  | Total |  |  |  |  | 50 |  | 125 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 114 | 116
18 | Bhilai | CSPTCL | Raipur | 1 | 13 | Twin ACSR Moose | - | - | - |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Seoni | 1 | 230 | Twin ACSR Moose | 50 | - | - |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Bhatapara | 1 | 93 | Twin ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Raita | 1 | 56 | Twin ACSR Moose | - | - |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Raita | 2 | 56 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Raita | 3 | 56 | Twin ACSR Moose | - | - |  |  |  | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Bhadrawati | 1 | 322 | Twin ACSR Moose | 80 | - |  |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 1 | 114 | 116
|  |  | Koradi | 1 | 272 | Twin ACSR Moose | 50 | - |  |  |  | 205 | 0 | 1 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Korba (W)-Ext | 1 | 220 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Korba-NTPC | 1 | 197 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 114 | 116
|  |  | Korba-NTPC | 2 | 192 | Twin ACSR Moose | 50 | - |  |  |  | 125 | 0 | 1 | 0 | 0 | 0 | 0 | 114 | 116
|  | Total |  |  |  |  | 330 | [5 empty] | 0 | 5 | 0 | 0 | 0 | 1 | 126 | 128
19 | Bhopal-BDTCL | BDTCL | Bhopal (MP) | 1 | 9 | Twin ACSR Moose | - | - | 1X125 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 128
|  |  | Bhopal (MP) | 2 | 9 | Twin ACSR Moose | - | - |  |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 128
|  | Total |  |  |  |  | - | - | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 131
20 | Bhopal-MP | MPPTCL | Bina-MP | 1 | 289 | Twin ACSR Moose | - | - | 1X125+1x80 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 131
|  |  | Bina-MP | 2 | 273 | Twin ACSR Moose | - | - |  |  |  | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 131
|  |  | Itarsi | 1 | 98 | Twin ACSR Moose | - | - |  |  |  | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 131
|  |  | Itarsi | 2 | 98 | Twin ACSR Moose | - | - |  |  |  | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 131
|  |  | Damoh | 1 | 214 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 129 | 131
|  |  | Damoh | 2 | 214 | Twin ACSR Moose | 50 | - |  |  |  | 188 | 0 | 1 | 0 | 0 | 0 | 0 | 129 | 131
|  |  | Bhopal-BDTCL | 1 | 9 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 131
|  |  | Bhopal-BDTCL | 2 | 9 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 131
|  | Total |  |  |  |  | 100 |  | 205 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 138 | 140
21 | Bhusawal (Khadka) | MSETCL | Bableshwar | 1 | 220 | Twin ACSR Moose | - | - | 1X50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Aurangabad-M(Waluj) | 1 | 238 | Twin ACSR Moose | - | - |  |  |  | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Akola | 1 | 182 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Deepnagar | 1 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Deepnagar | 2 | 15 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 140
|  |  | Koradi | 2 | 343 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 138 | 140
|  | Total |  |  |  |  | 100 |  | 50 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 145 | 147
22 | Bilaspur | PGCIL | ACBIL | 1 | 56 | Twin ACSR Moose | - | - | - |  |  | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 147
|  |  | MCCPL | 1 | 45 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 147
|  |  | Pathadi | 1 | 31 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 147
|  |  | Pathadi | 2 | 31 | Twin ACSR Moose | - | - |  |  |  | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 147
|  | Total |  |  |  |  | - | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 152
23 | Bina-MP | MPPTCL | JP-Bina | 1 | 20 | Twin ACSR Moose | - | - | 1X50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 152
|  |  | Bina-PG | 1 | 3 | Twin ACSR Moose | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 152
|  |  | Bina-PG | 2 | 3 | Twin ACSR Moose | - | - |  |  |  | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 152
|  |  | Bina-PG | 3 | 3 | Twin ACSR Moose | - | - |  |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 152
|  |  | Bina-PG | 4 | 3 | Twin ACSR Moose | - | - |  |  |  | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 152
|  |  | Bhopal | 1 | 289 | Twin ACSR Moose | 50 | - |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 150 | 152
|  |  | Bhopal | 2 | 273 | Twin ACSR Moose | 50 | - |  |  |  | 80 | 0 | 1 | 0 | 0 | 0 | 0 | 150 | 152
|  | Total |  |  |  |  | 100 |  | 50 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 158 | 160
24 | Bina-NHPTL |  | Bina-PG | 1 | 0.4 | Twin ACSR Moose | - | - | - | WRTS-2 | WRTS-2 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 160
|  |  | Satna | 3 | 272 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 160
|  | Total | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 163
25 | Bina-NTS | PGCIL | Bina-PG | 1 | 1 | Twin ACSR Moose | - | - | - |  |  | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 163
|  |  | Satna | 3 | 272 | Twin ACSR Moose | - | - |  |  |  | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 163
|  | Total |  |  |  |  | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
26 | Bina-PG | PGCIL | Shujalpur | 1 | 200 | Twin ACSR Moose | 63 | Yes | 1X125 |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 164 | 166
|  |  | Shujalpur | 2 | 200 | Twin ACSR Moose | 63 | Yes |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 164 | 166
|  |  | Bina-MP | 1 | 3 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Bina-MP | 2 | 3 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Bina-MP | 3 | 3 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Bina-MP | 4 | 3 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Bina-NHPTL | 1 | 0.4 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Satna | 1 | 276 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Satna | 2 | 276 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Satna | 3 | 273 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | Satna | 4 | 273 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 164 | 166
|  |  | JP-Bina | 1 | 20 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 166
|  | Total |  |  |  |  | 326 |  | 125 |  |  |  | 0 | 4 | 2 | 0 | 0 | 0 | 177 | 179
27 | Birsingpur | MPPGCL | Katni | 1 | 118 | Twin ACSR Moose | - | - | 1X50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 179
|  |  | Katni | 2 | 118 | Twin ACSR Moose | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 177 | 179
|  |  | Vandana | 1 | 215 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 179
|  |  | Damoh | 1 | 227 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 179
|  |  | Damoh | 2 | 227 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 179
|  |  | Korba-NTPC | 2 | 260 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 177 | 179
|  | Total |  |  |  |  | 113 |  | 50 |  |  |  | 0 | 1 | 0 | 1 | 0 | 0 | 184 | 186
28 | Boisar | PGCIL | Aurangabad-PG | 1 | 327 | Twin ACSR Moose | 80 | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 184 | 186
|  |  | Aurangabad-PG | 2 | 327 | Twin ACSR Moose | 80 | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 184 | 186
|  |  | Padghe | 1 | 101 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 186
|  |  | Tarapur-3&4 | 1 | 21 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 186
|  |  | Tarapur-3&4 | 2 | 21 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 186
|  |  | Vapi | 1 | 91 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 186
|  |  | Kala | 1 | 61 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 186
|  |  | Magarawada | 1 | 97 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 186
|  | Total |  |  |  |  | 160 |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 2 | 193 | 195
29 | CGPL | CGPL | Jetpur | 1 | 334 | Triple ACSR Snowbird | 63 | Yes | 1x63 | WRTS-2 | GETCO |  | 0 | 0 | 1 | 0 | 0 | 0 | 193 | 195
|  |  | Jetpur | 2 | 334 | Triple ACSR Snowbird | 63 | Yes |  | WRTS-2 | GETCO |  | 0 | 0 | 1 | 0 | 0 | 0 | 193 | 195
|  |  | Bachau | 1 | 100 | Triple ACSR Snowbird | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 195
|  |  | Bachau | 2 | 100 | Triple ACSR Snowbird | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 195
|  |  | Bachau | 3 | 122 | Triple ACSR Snowbird | 63 | Yes |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 1 | 0 | 0 | 0 | 193 | 195
|  |  | Bachau | 4 | 122 | Triple ACSR Snowbird | 63 | Yes |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 1 | 0 | 0 | 0 | 193 | 195
|  | Total |  |  |  |  | 252 |  | 63 |  |  |  | 0 | 0 | 4 | 0 | 0 | 0 | 200 | 202
30 | Chakan | MSETCL | Pune-PG | 1 | 18 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 202
|  |  | Lonikhand | 1 | 37 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 202
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 205
31 | Champa | PGCIL | KSK Mahanadi | 3 | 27 | Quad ACSR Moose | - | - | 1x80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 205
|  |  | KSK Mahanadi | 4 | 27 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 205
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 208
32 | Chandrapur | MSETCL | Bhadrawati | 1 | 20 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 208
|  |  | Bhadrawati | 2 | 20 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 208
|  |  | Bhadrawati | 3 | 22 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 208
|  |  | Bhadrawati | 4 | 22 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 208
|  |  | Khaparkheda | 1 | 156 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 208
|  |  | Parli-M | 3 | 371 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 206 | 208
|  |  | Chandrapur-II | 1 | 1 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 206 | 208
|  |  | Chandrapur-II | 2 | 1 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 206 | 208
|  | Total |  |  |  |  | 150 |  | - |  |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 215 | 217
33 | Chandrapur-GCR | MSETCL | Chandrapur-II | 1 | 2 | Quad AAAC Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 217
|  |  | Chandrapur-II | 2 | 2 | Quad AAAC Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 217
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
34 | Chandrapur-II | MSETCL | Dhariwal | 1 | 8 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Dhariwal | 2 | 8 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Nanded | 1 | 257 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Chandrapur | 1 | 1 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Chandrapur | 2 | 1 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Chandrapur-GCR | 1 | 2 | Quad AAAC Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Chandrapur-GCR | 2 | 2 | Quad AAAC Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Parli-M | 1 | 357 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Warora | 1 | 45 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  |  | Warora | 2 | 45 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 220
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 231
35 | Charnaka | GETCO | - | - | - | - | - | - | 1x125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 231
|  | Total | [6 empty] | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 233
36 | Chhegaon | MPPTCL | Julwania | 1 | 114 | Twin ACSR Moose | - | - | 1x50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 233
|  |  | Malwa | 1 | 53 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 233
|  | Total |  |  |  |  | - |  | 50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
37 | Chorania | GETCO | Kosamba | 1 | 230 | Twin ACSR Moose | 50 | - | 1X50 + 1X125 | GETCO | GETCO |  | 0 | 1 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | Kosamba | 2 | 230 | Twin ACSR Moose | 50 | - |  | GETCO | GETCO |  | 0 | 1 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | Amreli | 1 | 164 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | Asoj | 1 | 177 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | Asoj | 2 | 166 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | CGPL | 1 | 314 | Triple ACSR Snowbird | 63 | - |  | WRTS-2 | CGPL |  | 0 | 0 | 0 | 1 | 0 | 0 | 234 | 236
|  |  | Hadala | 1 | 166 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | Kasor | 1 | 103 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | Mansar | 1 | 94 | Triple ACSR Snowbird | 63 | - |  | WRTS-2 | GETCO |  | 0 | 0 | 0 | 1 | 0 | 0 | 234 | 236
|  |  | Ranchodpura | 1 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
|  |  | Ranchodpura | 2 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 236
|  | Total |  |  |  |  | 226 |  | 175 |  |  |  | 0 | 2 | 0 | 2 | 0 | 0 | 246 | 248
38 | Damoh | PGCIL | Birsinghpur | 1 | 227 | Twin ACSR Moose | 50 | - | 1X63 + 1X125 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 246 | 248
|  |  | Birsinghpur | 2 | 227 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 246 | 248
|  |  | Katni | 1 | 118 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 246 | 248
|  |  | Bhopal | 1 | 214 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 248
|  |  | Bhopal | 2 | 214 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 248
|  | Total |  |  |  |  | 150 |  | 188 |  |  |  | 0 | 3 | 0 | 0 | 0 | 0 | 252 | 254
39 | DB-Power | DB-Power | Raigarh-PS(Kotra) | 1 | 18 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 254
|  |  | Raigarh-PS(Kotra) | 2 | 18 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 254
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 257
40 | Deepnagar | MSETCL | Aurangabad-M(Waluj) | 2 | 185 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 257
|  |  | Bhusawal (Khadka) | 1 | 15 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 257
|  |  | Bhusawal (Khadka) | 2 | 15 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 257
|  |  | Taptithanda | 1 | 203 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 257
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
41 | Dehgam | PGCIL | Gandhar | 1 | 157 | Twin ACSR Moose | - | - | 1X63 + 1X125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Gandhar | 2 | 157 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Pirana-PG | 1 | 56 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Pirana-PG | 2 | 56 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Sami | 1 | 152 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Sami | 2 | 152 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Ranchodpura | 1 | 62 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Ranchodpura | 2 | 62 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Wanakbori | 1 | 68 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Nagda | 1 | 331 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Nagda | 2 | 331 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 260 | 262
|  |  | Soja | 1 | 41 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 262
|  | Total |  |  |  |  | 100 |  | 188 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 273 | 275
42 | DGEN | DGEN | Navsari | 1 | 105 | Twin ACSR Moose | - | - | 1X125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 275
|  |  | Navsari | 2 | 105 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 275
|  | Total |  |  |  |  | - |  | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 278
43 | Dhariwal | DIL | Parli-PG | 1 | 390 | Twin ACSR Moose | - | - | 1x80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 278
|  |  | Bhadrawati | 1 | 15 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 278
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 281
44 | Dhariwal-MS | DIL | Chandrapur-II | 1 | 8 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 281
|  |  | Chandrapur-II | 2 | 8 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 281
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 284
45 | Dhule-BDTCL | BDTCL | Dhule-MS | 1 | 18 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 284
|  |  | Dhule-MS | 2 | 18 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 284
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 287
46 | Dhule-MS | MSETCL | Dhule-BDTCL | 1 | 18 | Twin ACSR Moose | - | - | 1x80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 287
|  |  | Dhule-BDTCL | 2 | 18 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 287
|  |  | Bableshwar | 1 | 170 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 287
|  |  | Bableshwar | 2 | 170 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 287
|  |  | Khandwa | 1 | 262 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 285 | 287
|  |  | Khandwa | 2 | 262 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 285 | 287
|  |  | SSP | 1 | 236 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 285 | 287
|  |  | SSP | 2 | 236 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 285 | 287
|  | Total |  |  |  |  | 200 |  | 80 |  |  |  | 2 | 2 | 0 | 0 | 0 | 0 | 294 | 296
47 | Ektuni (Aurangabad(3)) | MSETCL | Bableshwar | 1 | 127 | Quad ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | Bableshwar | 2 | 127 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | Taptithanda | 1 | 5 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  |  | Taptithanda | 2 | 5 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 296
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 301
48 | EMCO | GMR | Bhadrawati | 1 | 28 | Twin ACSR Moose | - | - | 1X80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 301
|  |  | Bhadrawati | 2 | 28 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 301
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 304
49 | Essar_Mahan | ESSAR | Korba-NTPC | 1 | 218 | Twin ACSR Moose | - | - | 1X80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 304
|  |  | Vindhyachal | 1 | 41 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 304
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
50 | Gandhar | NTPC | Navsari | 1 | 106 | Twin ACSR Moose | - | - | 1X50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
|  |  | Kosamba | 1 | 93 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
|  |  | Hazira | 1 | 97 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
|  |  | Hazira | 2 | 97 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
|  |  | GPEC | 1 | 13 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
|  |  | Sugen | 1 | 64 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 305 | 307
|  |  | Dehgam | 1 | 157 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
|  |  | Dehgam | 2 | 157 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 307
|  | Total |  |  |  |  | 50 |  | 50 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 314 | 316
51 | GMR-CG | GMR | Raipur-PS(Durg) | 1 | 65 | Twin ACSR Moose | - | - | 1x125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 316
|  |  | Raipur-PS(Durg) | 2 | 65 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 316
|  | Total | [6 empty] | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 319
52 | GPEC | GPEC | Kasor | 1 | 98 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 319
|  |  | Gandhar | 1 | 13 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 319
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 322
53 | Gwalior | PGCIL | - | - | - | - | - | - | 3x125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 322
|  | Total |  |  |  |  | - |  | 375 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
54 | Hadala | GETCO | Versana | 1 | 159 | Twin ACSR Moose | - | - | 1X50 + 1X125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | Vadinar | 1 | 113 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | Vadinar | 2 | 113 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | Chorania | 1 | 166 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | Amreli | 1 | 165 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 324
|  |  | APL-Mundra | 1 | 233 | Twin ACSR Moose | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 322 | 324
|  | Total |  |  |  |  | 63 |  | 175 |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 329 | 331
55 | Hazira | ESSAR | Gandhar | 1 | 97 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 331
|  |  | Gandhar | 2 | 97 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 331
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 334
56 | IEPL | IEPL | Warora | 1 | 150 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 334
|  |  | Koradi-II | 1 | 94 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 334
|  | Total | [6 empty] | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 337
57 | Indira Sagar | MPPTCL | Indore-MP | 1 | 79 | Quad ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 337
|  |  | Indore-MP | 2 | 80 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 337
|  |  | Nagda | 1 | 188 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 337
|  |  | Satpura | 1 | 189 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 337
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 342
58 | Indore-MP | MPPTCL | Indore-PG | 1 | 50 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Indore-PG | 2 | 50 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Nagda | 1 | 108 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Asoj | 1 | 289 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Asoj | 2 | 273 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Indira Sagar | 1 | 79 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Indira Sagar | 2 | 80 | Quad ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Itarsi | 1 | 207 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 340 | 342
|  |  | Itarsi | 2 | 214 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 340 | 342
|  | Total |  |  |  |  | 250 | - | - |  |  |  | 0 | 5 | 0 | 0 | 0 | 0 | 350 | 352
59 | Indore-PG | PGCIL | Indore-MP | 1 | 50 | Twin ACSR Moose | - | - | 1X125 + 1X63 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Indore-MP | 2 | 50 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Pithampur | 1 | 150 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Pithampur | 2 | 150 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Khandwa | 1 | 169 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  |  | Khandwa | 2 | 169 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 350 | 352
|  | Total |  |  |  |  | 100 |  | 188 |  |  |  | 2 | 0 | 0 | 0 | 0 | 0 | 357 | 359
60 | Itarsi | PGCIL | Indore-MP | 1 | 207 | Twin ACSR Moose | 50 | - | 2X125 + 1X50 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Indore-MP | 2 | 214 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Khandwa | 1 | 197 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Khandwa | 2 | 197 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Bhopal-MP | 1 | 98 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Bhopal-MP | 2 | 98 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Jabalpur | 1 | 232 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Jabalpur | 2 | 232 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Jabalpur | 3 | 234 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Jabalpur | 4 | 234 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 357 | 359
|  |  | Satpura | 1 | 79 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 359
|  | Total |  |  |  |  | 400 |  | 300 |  |  |  | 2 | 6 | 0 | 0 | 0 | 0 | 369 | 371
61 | Jabalpur | PGCIL | Itarsi | 1 | 232 | Twin ACSR Moose | 50 | - | 1X125 + 1X63 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 369 | 371
|  |  | Itarsi | 2 | 232 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 369 | 371
|  |  | Itarsi | 3 | 234 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 369 | 371
|  |  | Itarsi | 4 | 234 | Twin ACSR Moose | 50 | Yes |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 369 | 371
|  |  | Sasan | 1 | 340 | Twin ACSR Moose | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 369 | 371
|  |  | Jabalpur-PS | 1 | 16 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 371
|  |  | Jabalpur-PS | 2 | 16 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 371
|  |  | Vindhyachal | 1 | 360 | Twin ACSR Moose | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 369 | 371
|  |  | Vindhyachal | 2 | 360 | Twin ACSR Moose | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 369 | 371
|  |  | Vindhyachal | 4 | 389 | Twin ACSR Moose | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 369 | 371
|  | Total |  |  |  |  | 452 |  | 188 |  |  |  | 2 | 2 | 0 | 4 | 0 | 0 | 380 | 382
62 | Jabalpur (PS) | PGCIL | MB Power | 1 | 246 | Triple ACSR Snowbird | 50 | - | 2X125 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | MB Power | 2 | 246 | Triple ACSR Snowbird | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | Jhabua Power | 1 | 65 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | Jhabua Power | 2 | 65 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | Jabalpur | 1 | 16 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  |  | Jabalpur | 2 | 16 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 382
|  | Total |  |  |  |  | 100 |  | 250 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 387 | 389
63 | Jagdalpur | CSPTCL | Raita | 2 | 328 | Twin ACSR Moose | 80 | Yes |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 1 | 0 | 387 | 389
|  | Total |  |  |  |  | 80 | [5 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 389 | 391
64 | Jaigad | MSETCL | New koyna | 1 | 55 | Twin ACSR Moose | - | - | 2x50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 391
|  |  | New koyna | 2 | 55 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 391
|  |  | Karad | 1 | 111 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 391
|  |  | Karad | 2 | 111 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 391
|  | Total |  |  |  |  | - |  | 100 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 396
65 | Jejuri | MSETCL | Koyna stage-IV | 1 | 172 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 396
|  |  | Lonikhand | 1 | 48 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 396
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
66 | Jetpur | GETCO | Amreli | 1 | 96 | Twin ACSR Moose | - | - | 1X50 + 1X63 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
|  |  | Amreli | 2 | 96 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 399
|  |  | CGPL | 1 | 334 | Triple ACSR Snowbird | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 397 | 399
|  |  | CGPL | 2 | 334 | Triple ACSR Snowbird | 63 | - |  |  |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 397 | 399
|  | Total |  |  |  |  | 126 |  | 113 |  |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 402 | 404
67 | Jhabua Power | Jhabua Power | Jabalpur (PS) | 1 | 65 | Twin ACSR Moose | - | - | 1x125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  |  | Jabalpur (PS) | 2 | 65 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 404
|  | Total |  |  |  |  | - |  | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 407
68 | JP-Bina | Jaypee | Bina-MP | 1 | 20 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 407
|  |  | Bina-PG | 1 | 20 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 407
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 410
69 | JPL | JPL | Raipur | 1 | 258 | Twin ACSR Moose | - | - | 1x125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 410
|  |  | Raipur | 2 | 258 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 410
|  |  | JPL_extn(Tamnar) | 1 | 2 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 410
|  | Total | [6 empty] | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 414
70 | JPL_extn(Tamnar) | JPL | Tamnar-PS | 1 | 10 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 414
|  |  | Tamnar-PS | 2 | 10 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 414
|  |  | Tamnar-PS | 3 | 10 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 414
|  |  | Tamnar-PS | 4 | 10 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 414
|  |  | JPL | 1 | 2 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 414
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 420
71 | JP-Nigrie | Jaypee | Satna | 1 | 161 | Twin ACSR Moose | - | - | 1X125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 420
|  |  | Satna | 2 | 161 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 420
|  | Total |  |  |  |  | - |  | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
72 | Julwania | MPPTCL | Chhegaon | 1 | 114 | Twin ACSR Moose | - | - | 1x50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
|  |  | Malwa | 1 | 170 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 423
|  | Total |  |  |  |  | - |  | 50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 426
73 | Kala | PGCIL | Vapi | 1 | 49 | Twin ACSR Moose | - | - | 1X80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 426
|  |  | Vapi | 2 | 52 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 426
|  |  | Boisar | 1 | 61 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 426
|  |  | Magarawada | 2 | 53 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 426
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 431
74 | Kalwa | MSETCL | Padghe | 1 | 72 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 431
|  |  | Padghe | 2 | 72 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 431
|  |  | Kharghar | 1 | 28 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 431
|  |  | Pune-PG | 1 | 104 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 431
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
75 | Karad | MSETCL | Kolhapur | 1 | 105 | Twin ACSR Moose | - | - | 1X80 | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  |  | Kolhapur | 2 | 105 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  |  | Jaigad | 1 | 111 | Twin ACSR Moose | - | - |  | MSETCL | JAIGAD-IPP |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  |  | Jaigad | 2 | 111 | Twin ACSR Moose | - | - |  | MSETCL | JAIGAD-IPP |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  |  | New Koyna | 1 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  |  | New Koyna | 2 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 436
|  |  | Lonikhand | 1 | 161 | Twin ACSR Moose | 80 | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 1 | 434 | 436
|  | Total |  |  |  |  | 80 |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 442 | 444
76 | Kasor | GETCO | Chorania | 1 | 103 | Twin ACSR Moose | - | - | 1X50 + 1X125 | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 444
|  |  | GPEC | 1 | 98 | Twin ACSR Moose | - | - |  | GPEC | GPEC |  | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 444
|  |  | Rajgarh | 1 | 243 | Twin ACSR Moose | 50 | - |  | WRTGPL | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 442 | 444
|  |  | Rajgarh | 2 | 243 | Twin ACSR Moose | 50 | - |  | WRTGPL | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 442 | 444
|  |  | SSP | 1 | 146 | Twin ACSR Moose | - | - |  | GETCO | SSNNL |  | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 444
|  | Total |  |  |  |  | 100 |  | 175 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 448 | 450
77 | Katni | MPPTCL | Birsingpur | 1 | 118 | Twin ACSR Moose | - | - | - | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 448 | 450
|  |  | Birsingpur | 2 | 118 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 448 | 450
|  |  | Damoh | 1 | 118 | Twin ACSR Moose | - | - |  | MPPTCL | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 448 | 450
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 454
78 | Khandwa | PGCIL | Dhule-MS | 1 | 262 | Twin ACSR Moose | 50 | - | 2X125 | WRTS-2 | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Dhule-MS | 2 | 262 | Twin ACSR Moose | 50 | - |  | WRTS-2 | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Rajgarh | 1 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Rajgarh | 2 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Betul | 1 | 169 | Quad ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Betul | 2 | 169 | Quad ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Indore-PG | 1 | 169 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Indore-PG | 2 | 169 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Itarsi | 1 | 197 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Itarsi | 2 | 197 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 454
|  |  | Seoni | 1 | 352 | Quad AAAC Moose | 80 | Yes |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 452 | 454
|  |  | Seoni | 2 | 352 | Quad AAAC Moose | 80 | Yes |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 452 | 454
|  | Total |  |  |  |  | 360 |  | 250 |  |  |  | 0 | 4 | 0 | 0 | 2 | 0 | 465 | 467
79 | Khaparkheda | MSETCL | Chandrapur | 1 | 156 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 467
|  |  | Koradi | 1 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 467
|  |  | Koradi | 2 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 467
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 469 | 471
80 | Kharghar | MSETCL | Pune-PG | 1 | 185 | Twin ACSR Moose | - | - | 1X80 | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 469 | 471
|  |  | Kalwa | 1 | 28 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 469 | 471
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 474
81 | Kolhapur | MSETCL | Kolhapur-PG | 1 | 39 | Twin ACSR Moose | - | - | 1X80 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 474
|  |  | Kolhapur-PG | 2 | 39 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 474
|  |  | Sholapur-PG | 1 | 220 | Twin ACSR Moose | - | - |  | WRTMPL | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 474
|  |  | Sholapur-PG | 2 | 220 | Twin ACSR Moose | - | - |  | WRTMPL | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 474
|  |  | Karad | 1 | 105 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 474
|  |  | Karad | 2 | 105 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 474
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 481
82 | Kolhapur-PG | PGCIL | Mapusa | 1 | 156 | Twin ACSR Moose | - | - | 1x125 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 481
|  |  | Mapusa | 2 | 156 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 481
|  |  | Kolhapur | 1 | 39 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 481
|  |  | Kolhapur | 2 | 39 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 481
|  | Total |  |  |  |  | - |  | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 484 | 486
83 | Koradi | MSETCL | Bhusawal | 2 | 343 | Twin ACSR Moose | 50 | - | 1X50 | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 484 | 486
|  |  | Satpura | 1 | 149 | Twin ACSR Moose | - | - |  | WRTS-1 | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 484 | 486
|  |  | Bhilai | 1 | 272 | Twin ACSR Moose | 50 | - |  | WRTS-1 | CSPTCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 484 | 486
|  |  | Khaparkheda | 1 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 484 | 486
|  |  | Khaparkheda | 2 | 10 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 484 | 486
|  |  | Nandgaonpeth | 1 | 140 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 484 | 486
|  | Total |  |  |  |  | 100 |  | 50 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 491 | 493
84 | Koradi-II | MSETCL | IEPL | 2 | 94 | Twin ACSR Moose | - | - | - | MSETCL | IEPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 491 | 493
|  |  | Koradi-II | 1 | 38 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 491 | 493
|  |  | Koradi-II | 2 | 39 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 491 | 493
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 497
85 | Korba (W) | CSPTCL | Korba-NTPC | 1 | 14 | Twin ACSR Moose | - | - | - | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 497
|  |  | Raita | 1 | 144 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 497
|  |  | Korba (W)-Ext | 1 | 1 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 497
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 499 | 501
86 | Korba (W)-Ext | CSPTCL | Bhilai | 1 | 220 | Twin ACSR Moose | - | - | - | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 499 | 501
|  |  | Marwa | 1 | 60 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 499 | 501
|  |  | Korba (W) | 1 | 1 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 499 | 501
|  | Total | [6 empty] | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
87 | Korba-NTPC | NTPC | Bhilai | 1 | 197 | Twin ACSR Moose | - | - | - | WRTS-1 | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Bhilai | 2 | 192 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Raipur | 1 | 212 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Raipur | 2 | 212 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Sipat | 1 | 100 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Essar_Mahan | 1 | 218 | Twin ACSR Moose | - | - |  | WRTS-1 | ESSAR |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Vindhyachal | 2 | 289 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Bhatapara | 1 | 124 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Birsingpur | 2 | 260 | Twin ACSR Moose | 50 | - |  | WRTS-2 | BALCO |  | 0 | 1 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Vandana | 1 | 18 | Twin ACSR Moose | 50 | - |  | WRTS-2 | Vandana Vidyut |  | 0 | 1 | 0 | 0 | 0 | 0 | 503 | 505
|  |  | Korba (W) | 1 | 14 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 505
|  | Total |  |  |  |  | 100 |  | - |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 515 | 517
88 | Kosamba | GETCO | Asoj | 1 | 122 | Twin ACSR Moose | - | - | 1X80 | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 517
|  |  | Chorania | 1 | 230 | Twin ACSR Moose | 63 | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 1 | 0 | 0 | 515 | 517
|  |  | Chorania | 2 | 230 | Twin ACSR Moose | 63 | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 1 | 0 | 0 | 515 | 517
|  |  | Gandhar | 1 | 93 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 517
|  |  | Ukai | 1 | 81 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 517
|  |  | Ukai | 2 | 68 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 517
|  | Total |  |  |  |  | 126 |  | 80 |  |  |  | 0 | 0 | 0 | 2 | 0 | 0 | 522 | 524
89 | Koyna stage-IV | MSETCL | Lonikhand | 1 | 183 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 524
|  |  | New Koyna | 1 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 524
|  |  | New Koyna | 2 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 524
|  |  | Jejuri | 1 | 172 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 522 | 524
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 527 | 529
90 | KSK Mahanadi | KSK | Champa | 3 | 27 | Quad ACSR Moose | - | - | - | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 527 | 529
|  |  | Champa | 4 | 27 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 527 | 529
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 532
91 | KWPCL | KWPCL | Raipur | 1 | 18 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 532
|  |  | Raigarh | 1 | 217 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 532
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 533 | 535
92 | Lara | NTPC | Raigarh-PS(Kotra) | 1 | 18 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 533 | 535
|  |  | Raigarh-PS(Kotra) | 2 | 18 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 533 | 535
|  |  | Champa | 1 | 112 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 533 | 535
|  |  | Champa | 2 | 112 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 533 | 535
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 540
93 | Lonikhand | MSETCL | Jejuri | 1 | 48 | Twin ACSR Moose | - | - | 1X50 | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 540
|  |  | Chakan | 1 | 37 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 538 | 540
|  |  | Pune-PG | 1 | 40 | Twin ACSR Moose | - | - |  | MSETCL | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 540
|  |  | Karad | 1 | 161 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 540
|  |  | Koyna stage-IV | 1 | 183 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 540
|  |  | Lonikhand-II | 1 | 1 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 540
|  |  | Lonikhand-II | 2 | 1 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 540
|  | Total |  |  |  |  | 50 |  | 50 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 546 | 548
94 | Lonikhand-II | MSETCL | Lonikhand | 1 | 1 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 546 | 548
|  |  | Lonikhand | 2 | 1 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 546 | 548
|  |  | Parli-M | 1 | 284 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 546 | 548
|  |  | Parli-M | 2 | 284 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 546 | 548
|  | Total |  |  |  |  | 100 |  | - |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 551 | 553
95 | Magarawada | PGCIL | Boisar | 1 | 97 | Twin ACSR Moose | - | - | 1x80 | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 553
|  |  | Kala | 2 | 53 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 553
|  |  | Navasari | 1 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 553
|  |  | Navasari | 2 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 553
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 558
96 | Malwa | MPPTCL | Chhegaon | 1 | 53 | Twin ACSR Moose | - | - | - | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 558
|  |  | Pithampur | 1 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 558
|  |  | Pithampur | 2 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 558
|  |  | Julwania | 1 | 170 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 558
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 563
97 | Mansar | GETCO | Chorania | 1 | 94 | Triple ACSR Snowbird | - | - | 1x63 | WRTS-2 | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 563
|  |  | Bachau | 1 | 128 | Triple ACSR Snowbird | - | - |  | WRTS-2 | CGPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 563
|  | Total |  |  |  |  | - |  | 63 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 566
98 | Mapusa | PGCIL | Kolhapur-PG | 1 | 156 | Twin ACSR Moose | - | - | 1X50 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 566
|  |  | Kolhapur-PG | 2 | 156 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 566
|  | Total |  |  |  |  | - |  | 50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
99 | Marwa | CSPTCL | Korba (W)-Ext | 1 | 60 | Twin ACSR Moose | - | - | - | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  |  | Raita | 1 | 141 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  |  | Raita | 2 | 141 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 567 | 569
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 571 | 573
100 | MB Power | MB Power | Jabalpur (PS) | 1 | 246 | Triple ACSR Snowbird | 50 | Yes | 1x125 | WRTS-2 | WRTS-2 |  | 1 | 0 | 0 | 0 | 0 | 0 | 571 | 573
|  |  | Jabalpur (PS) | 2 | 246 | Triple ACSR Snowbird | 50 | Yes |  | WRTS-2 | WRTS-2 |  | 1 | 0 | 0 | 0 | 0 | 0 | 571 | 573
|  | Total |  |  |  |  | 100 |  | 125 |  |  |  | 2 | 0 | 0 | 0 | 0 | 0 | 574 | 576
101 | MCCPL | ACBIL | Bilaspur | 1 | 45 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  |  | ACBIL | 1 | 16 | Twin ACSR Moose | - | - |  | WRTS-1 | ACBIL |  | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 576
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 579
102 | Mouda | NTPC | Wardha | 1 | 124 | Quad ACSR Moose | - | - | 2x80 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 579
|  |  | Wardha | 2 | 124 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 579
|  |  | Betul | 1 | 193 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 579
|  |  | Betul | 2 | 193 | Quad ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 579
|  | Total |  |  |  |  | - |  | 160 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 584
103 | Nagda | MPPTCL | Dehgam | 1 | 331 | Twin ACSR Moose | 50 | - | 2X50 | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 582 | 584
|  |  | Dehgam | 2 | 331 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 582 | 584
|  |  | Shujalpur | 1 | 202 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 584
|  |  | Shujalpur | 2 | 152 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 584
|  |  | Indira Sagar | 1 | 188 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 584
|  |  | Indore-MP | 1 | 108 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 584
|  |  | Rajgarh | 1 | 104 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 582 | 584
|  |  | Rajgarh | 2 | 104 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 582 | 584
|  | Total |  |  |  |  | 200 |  | 100 |  |  |  | 0 | 4 | 0 | 0 | 0 | 0 | 591 | 593
104 | Nagothane | MSETCL | Padghe | 1 | 116 | Twin ACSR Moose | - | - | 1X80 | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 593
|  |  | Padghe | 2 | 116 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 593
|  |  | RGPPL | 1 | 136 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 593
|  |  | RGPPL | 2 | 136 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 593
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 598
105 | Nanded | MSETCL | Chandrapur-II | 1 | 257 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 598
|  |  | Chandrapur-II | 2 | 276 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 598
|  |  | Parli-M | 1 | 163 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 598
|  |  | Parli-M | 2 | 160 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 598
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 603
106 | Nandgaonpeth | Rattan India | Koradi-II | 1 | 140 | Twin ACSR Moose | - | - | 1x80 | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 603
|  |  | Akola | 1 | 117 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 603
|  |  | Akola(2) | 1 | 104 | Twin ACSR Moose | - | - |  | MEGPTCL | MEGPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 603
|  |  | Akola(2) | 2 | 104 | Twin ACSR Moose | - | - |  | MEGPTCL | MEGPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 603
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
107 | Navsari | PGCIL | DGEN | 1 | 105 | Twin ACSR Moose | - | - | 1X63 | TPL | DGEN |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  |  | DGEN | 2 | 105 | Twin ACSR Moose | - | - |  | TPL | DGEN |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  |  | Gandhar | 1 | 106 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  |  | Magarawada | 1 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  |  | Magarawada | 2 | 126 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  |  | Ukai | 1 | 83 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  |  | Kakrapar-3&4 | 1 | 38 | Twin ACSR Moose | - | - |  | WRTS-2 | NPCIL |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  |  | Kakrapar-3&4 | 2 | 38 | Twin ACSR Moose | - | - |  | WRTS-2 | NPCIL |  | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 608
|  | Total |  |  |  |  | - |  | 63 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
108 | New koyna | MSETCL | Jaigad | 1 | 55 | Twin ACSR Moose | - | - | - | MSETCL | JAIGAD-IPP |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  |  | Jaigad | 2 | 55 | Twin ACSR Moose | - | - |  | MSETCL | JAIGAD-IPP |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  |  | Karad | 1 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  |  | Karad | 2 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  |  | Koyna stage-IV | 1 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  |  | Koyna stage-IV | 2 | 14 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  |  | RGPPL | 1 | 60 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  |  | RGPPL | 2 | 60 | Twin ACSR Moose | - | - |  | MSETCL | RGPPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 617
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 626
109 | Nicol-II | TPL | Dehgam | 1 | 25 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 626
|  |  | Pirana-PG | 1 | 45 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 626
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 627 | 629
110 | NSPCL | NSPCL | Raipur | 1 | 14 | Twin ACSR Moose | - | - | - | NSPCL | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 627 | 629
|  |  | Raipur | 2 | 14 | Twin ACSR Moose | - | - |  | NSPCL | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 627 | 629
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
111 | Padghe | MSETCL | Boisar | 1 | 101 | Twin ACSR Moose | 50 | - | 1X80 | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Nagothane | 1 | 116 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Nagothane | 2 | 116 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Bableshwar | 1 | 174 | Twin ACSR Moose | - | - |  | MSETCL | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Bableshwar | 2 | 174 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Kalwa | 1 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Kalwa | 2 | 72 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Tarapur-3&4 | 1 | 91 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  |  | Tarapur-3&4 | 2 | 91 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 632
|  | Total |  |  |  |  | 50 |  | 80 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 640 | 642
112 | Parli-M | MSETCL | Lonikhand-II | 1 | 284 | Twin ACSR Moose | 50 | - | 1X50 | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 640 | 642
|  |  | Lonikhand-II | 2 | 284 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 640 | 642
|  |  | Sholapur-M | 1 | 182 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 640 | 642
|  |  | Chandrapur-II | 1 | 357 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 640 | 642
|  |  | Nanded | 1 | 163 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 640 | 642
|  |  | Parli-PG | 1 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 642
|  |  | Parli-PG | 2 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 642
|  |  | Chandrapur | 3 | 371 | Twin ACSR Moose | 50 | - |  | MSETCL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 640 | 642
|  | Total |  |  |  |  | 300 |  | 50 |  |  |  | 0 | 6 | 0 | 0 | 0 | 0 | 649 | 651
113 | Parli-PG | PGCIL | Pune-PG (Shikrapur) | 1 | 272 | Twin ACSR Moose | 50 | - | 1X63 + 1X125 | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 649 | 651
|  |  | Pune-PG (Shikrapur) | 2 | 272 | Twin ACSR Moose | 50 | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 649 | 651
|  |  | Sholapur-PG | 1 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 649 | 651
|  |  | Sholapur-PG | 2 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 649 | 651
|  |  | Bhadrawati | 1 | 388 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 649 | 651
|  |  | Dhariwal | 1 | 390 | Twin ACSR Moose | 63 | - |  | WRTS-1 | Dhariwal Infra |  | 0 | 0 | 0 | 1 | 0 | 0 | 649 | 651
|  |  | Parli-M | 1 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 649 | 651
|  |  | Parli-M | 2 | 5 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 649 | 651
|  |  | Wardha | 1 | 337 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 649 | 651
|  |  | Wardha | 2 | 337 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 649 | 651
|  | Total |  |  |  |  | 352 |  | 188 |  |  |  | 0 | 2 | 0 | 4 | 0 | 0 | 660 | 662
114 | Pathadi | LANCO | Bilaspur-PS | 1 | 31 | Twin ACSR Moose | - | - | - | LANCO | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 662
|  |  | Bilaspur-PS | 2 | 31 | Twin ACSR Moose | - | - |  | LANCO | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 662
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 663 | 665
115 | Pirana-PG | PGCIL | Dehgam | 1 | 56 | Twin ACSR Moose | - | - | 1X125 | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 663 | 665
|  |  | Dehgam | 2 | 56 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 663 | 665
|  |  | Pirana-T | 1 | 6 | Twin ACSR Moose | - | - |  | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 663 | 665
|  |  | Pirana-T | 2 | 6 | Twin ACSR Moose | - | - |  | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 663 | 665
|  |  | Vadodara-PS | 1 | 131 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 663 | 665
|  |  | Vadodara-PS | 2 | 131 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 663 | 665
|  | Total |  |  |  |  | - |  | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 670 | 672
116 | Pirana-T | TPL | Pirana-PG | 1 | 6 | Twin ACSR Moose | - | - | - | TPL | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 670 | 672
|  |  | Pirana-PG | 2 | 6 | Twin ACSR Moose | - | - |  | TPL | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 670 | 672
|  |  | Sugen | 1 | 212 | Twin ACSR Moose | 50 | - |  | TPL | TPL |  | 0 | 1 | 0 | 0 | 0 | 0 | 670 | 672
|  |  | Uno-Sugen | 1 | 209 | Twin ACSR Moose | 50 | - |  | TPL | TPL |  | 0 | 1 | 0 | 0 | 0 | 0 | 670 | 672
|  | Total |  |  |  |  | 100 |  | - |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 675 | 677
117 | Pithampur | MPPTCL | Indore-PG | 1 | 150 | Twin ACSR Moose | - | - | 1x50 | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 675 | 677
|  |  | Indore-PG | 2 | 150 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 675 | 677
|  |  | Malwa | 1 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 675 | 677
|  |  | Malwa | 2 | 136 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 675 | 677
|  | Total |  |  |  |  | - |  | 50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
118 | Pune-PG | PGCIL | Chakan | 1 | 18 | Twin ACSR Moose | - | - | 1x50 | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Kalwa | 1 | 104 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Lonikhand | 1 | 40 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Kharghar | 1 | 185 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Pune-PG(Shikrapur) | 1 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Pune-PG(Shikrapur) | 2 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Pune-PG(Shikrapur) | 2 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  |  | Pune-PG(Shikrapur) | 2 | 64 | Twin ACSR Moose | 50 | Yes |  | WRTMPL/WRTS-1 | WRTS-1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 680 | 682
|  | Total |  |  |  |  | 200 |  | 50 |  |  |  | 4 | 0 | 0 | 0 | 0 | 0 | 689 | 691
119 | Pune-PG(Shikrapur) | PGCIL | Pune-PG | 1 | 64 | Twin ACSR Moose | - | - | - | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 689 | 691
|  |  | Pune-PG | 2 | 64 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 689 | 691
|  |  | Pune-PG | 3 | 64 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 689 | 691
|  |  | Pune-PG | 4 | 64 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 689 | 691
|  |  | Aurangabad-M(Waluj) | 1 | 315 | Twin ACSR Moose | 50 | Yes |  | WRTMPL | MSETCL |  | 1 | 0 | 0 | 0 | 0 | 0 | 689 | 691
|  |  | Aurangabad-M(Waluj) | 2 | 315 | Twin ACSR Moose | 50 | Yes |  | WRTMPL | MSETCL |  | 1 | 0 | 0 | 0 | 0 | 0 | 689 | 691
|  |  | Parli-PG | 1 | 272 | Twin ACSR Moose | 50 | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 689 | 691
|  |  | Parli-PG | 2 | 272 | Twin ACSR Moose | 50 | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 689 | 691
|  | Total |  |  |  |  | 200 |  | - |  |  |  | 2 | 2 | 0 | 0 | 0 | 0 | 698 | 700
120 | Raigarh | PGCIL | India Bharath | 1 | 110 | Twin ACSR Moose | - | - | 1X63 + 1X125 | WRTS-1/ERTS-2 | ERTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Jharsuguda | 2 | 125 | Twin ACSR Moose | - | - |  | WRTS-1/ERTS-2 | ERTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Rourkela | 1 | 130 | Twin ACSR Moose | - | - |  | WRTS-1/ERTS-2 | ERTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Sterlite | 2 | 130 | Twin ACSR Moose | - | - |  | WRTS-1/ERTS-2 | ERTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Raipur | 1 | 217 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Raipur | 2 | 217 | Twin ACSR Moose | - | - |  | WRTS-1 | KWPCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Raipur | 3 | 221 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Raipur | 4 | 221 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Raigarh-PS(Kotra) | 1 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | KSK |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  |  | Raigarh-PS(Kotra) | 2 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | RKMPPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 698 | 700
|  | Total |  |  |  |  | - |  | 188 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
121 | Raigarh-PS(Kotra) | PGCIL | Athena | 1 | 25 | Quad ACSR Moose | - | - | 1X80 | ACPL | ACPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | Athena | 2 | 25 | Quad ACSR Moose | - | - |  | ACPL | ACPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | DB-Power | 1 | 18 | Twin ACSR Moose | - | - |  | DB-Power | DB-Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | DB-Power | 2 | 18 | Twin ACSR Moose | - | - |  | DB-Power | DB-Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | KWPCL | 1 | 19 | Twin ACSR Moose | - | - |  | KWPCL | KWPCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | KWPCL | 2 | 19 | Twin ACSR Moose | - | - |  | KWPCL | KWPCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | Lara | 1 | 18 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | Lara | 2 | 18 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | Raigarh | 1 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | Raigarh | 2 | 7 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | RKM | 1 | 27 | Quad ACSR Moose | - | - |  | RKM | RKM |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | RKM | 2 | 27 | Quad ACSR Moose | - | - |  | RKM | RKM |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | SKS | 1 | 28 | Twin ACSR Moose | - | - |  | WRTS-1 | SKS |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  |  | SKS | 2 | 28 | Twin ACSR Moose | - | - |  | WRTS-1 | SKS |  | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 711
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
122 | Raipur | PGCIL | Wardha | 1 | 371 | Quad ACSR Moose | 63 | - | 1X125 + 1X80 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 724 | 726
|  |  | Wardha | 2 | 371 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 724 | 726
|  |  | Raipur-PS(Durg) | 1 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Raipur-PS(Durg) | 2 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Bhadrawati | 1 | 333 | Twin ACSR Moose | 80 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 1 | 724 | 726
|  |  | Bhadrawati | 2 | 346 | Twin ACSR Moose | 50 | Yes |  | WRTS-1 | WRTS-1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Bhadrawati | 3 | 346 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 724 | 726
|  |  | Bhilai | 1 | 13 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | JPL | 1 | 258 | Twin ACSR Moose | 50 | - |  | JPL | JPL |  | 0 | 1 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | JPL | 2 | 258 | Twin ACSR Moose | 50 | - |  | JPL | JPL |  | 0 | 1 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Korba-NTPC | 1 | 212 | Twin ACSR Moose | 63 | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 1 | 0 | 0 | 724 | 726
|  |  | Korba-NTPC | 2 | 212 | Twin ACSR Moose | 63 | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 1 | 0 | 0 | 724 | 726
|  |  | NSPCL | 1 | 14 | Twin ACSR Moose | - | - |  | NSPCL | NSPCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | NSPCL | 2 | 14 | Twin ACSR Moose | - | - |  | NSPCL | NSPCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Raigarh | 1 | 217 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 724 | 726
|  |  | Raigarh | 1 | 217 | Twin ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 724 | 726
|  |  | Raigarh | 3 | 221 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Raigarh | 4 | 221 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Sipat | 1 | 149 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Sipat | 2 | 149 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  |  | Sipat | 3 | 156 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 726
|  | Total |  |  |  |  | 771 |  | 205 |  |  |  | 1 | 4 | 0 | 7 | 0 | 1 | 746 | 748
123 | Raipur-PS(Durg) | PGCIL | GMR-CG | 1 | 65 | Twin ACSR Moose | - | - | - | GMR | GMR-CG |  | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 748
|  |  | GMR-CG | 2 | 65 | Twin ACSR Moose | - | - |  | GMR | GMR-CG |  | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 748
|  |  | Raipur | 1 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 748
|  |  | Raipur | 2 | 22 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 748
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
124 | Raita | CSPTCL | Marwa | 1 | 141 | Twin ACSR Moose | - | - | - | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
|  |  | Marwa | 2 | 141 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
|  |  | Bhilai | 1 | 56 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
|  |  | Bhilai | 2 | 56 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
|  |  | Bhilai | 3 | 56 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
|  |  | Jagdalpur | 1 | 328 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
|  |  | Korba (W) | 1 | 144 | Twin ACSR Moose | - | - |  | CSPTCL | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 753
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 761
125 | Rajgarh | PGCIL | Nagda | 1 | 104 | Twin ACSR Moose | - | - | 1X125 | WRTS-2 | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  |  | Nagda | 2 | 104 | Twin ACSR Moose | - | - |  | WRTS-2 | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  |  | Kasor | 1 | 243 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  |  | Kasor | 2 | 243 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  |  | Khandwa | 1 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  |  | Khandwa | 2 | 221 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  |  | SSP | 1 | 178 | Twin ACSR Moose | 50 | Yes |  | MPPTCL | SSNNL |  | 1 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  |  | SSP | 2 | 178 | Twin ACSR Moose | 50 | Yes |  | MPPTCL | SSNNL |  | 1 | 0 | 0 | 0 | 0 | 0 | 759 | 761
|  | Total |  |  |  |  | 100 |  | 125 |  |  |  | 2 | 0 | 0 | 0 | 0 | 0 | 768 | 770
126 | Ranchodpura | GETCO | Zerda(Kansari) | 1 | 140 | Twin ACSR Moose | - | - | 1X50 + 1X125 | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 770
|  |  | Zerda(Kansari) | 2 | 140 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 770
|  |  | Chorania | 1 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 770
|  |  | Chorania | 2 | 103 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 770
|  |  | Bachau | 1 | 282 | Triple ACSR Snowbird | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 768 | 770
|  |  | Bachau | 2 | 282 | Triple ACSR Snowbird | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 768 | 770
|  |  | Dehgam | 1 | 62 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 770
|  |  | Dehgam | 2 | 62 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 770
|  | Total |  |  |  |  | 100 |  | 175 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 777 | 779
127 | RGPPL | RGPPL | New Koyna | 1 | 60 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 779
|  |  | New Koyna | 2 | 60 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 779
|  |  | Nagothane | 1 | 136 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 779
|  |  | Nagothane | 2 | 136 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 779
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 784
128 | RKM | RKM | Raigarh-PS(Kotra) | 1 | 27 | Quad ACSR Moose | - | - | 2x50 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 784
|  |  | Raigarh-PS(Kotra) | 2 | 27 | Quad ACSR Moose | - | - |  | WRTS-1 | KSK |  | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 784
|  | Total |  |  |  |  | - |  | 100 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 787
129 | Sami | APL | APL-Mundra | 1 | 282 | Twin ACSR Moose | 50 | - | 1x50 | ATIL | APL |  | 0 | 1 | 0 | 0 | 0 | 0 | 785 | 787
|  |  | APL-Mundra | 2 | 282 | Twin ACSR Moose | 50 | - |  | ATIL | APL |  | 0 | 1 | 0 | 0 | 0 | 0 | 785 | 787
|  |  | Dehgam | 1 | 152 | Twin ACSR Moose | - | - |  | ATIL | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 787
|  |  | Dehgam | 2 | 152 | Twin ACSR Moose | - | - |  | ATIL | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 787
|  | Total |  |  |  |  | 100 |  | 50 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 790 | 792
130 | Sasan | SPL | Jabalpur | 1 | 340 | Twin ACSR Moose | 50 | - | - | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 790 | 792
|  |  | Vindhyachal | 3 | 20 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 792
|  |  | Vindhyachal-PS | 1 | 8 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 792
|  |  | Vindhyachal-PS | 2 | 8 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 792
|  | Total |  |  |  |  | 50 |  | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
131 | Satna | PGCIL | Bina-PG | 1 | 276 | Twin ACSR Moose | 50 | - | 1X50 + 1X63 | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | Bina-PG | 2 | 276 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | Bina-NTS | 3 | 272 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | Bina-PG | 4 | 273 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | JP-Nigrie | 1 | 161 | Twin ACSR Moose | - | - |  | Jaypee | Jaypee |  | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | JP-Nigrie | 2 | 161 | Twin ACSR Moose | - | - |  | Jaypee | Jaypee |  | 0 | 0 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | Vindhyachal | 1 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | Vindhyachal | 2 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | Vindhyachal | 3 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  |  | Vindhyachal | 4 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | NTPC |  | 0 | 1 | 0 | 0 | 0 | 0 | 795 | 797
|  | Total |  |  |  |  | 400 |  | 113 |  |  |  | 0 | 8 | 0 | 0 | 0 | 0 | 806 | 808
132 | Satpura | MPPTCL | Indira sagar | 1 | 189 | Twin ACSR Moose | - | - | 2X63 | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Itarsi | 1 | 79 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Astha | 1 | 240 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Astha | 2 | 240 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Koradi | 1 | 149 | Twin ACSR Moose | 50 | - |  | WRTS-1 | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 806 | 808
|  |  | Seoni | 1 | 156 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 808
|  | Total |  |  |  |  | 50 |  | 126 |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 813 | 815
133 | Seoni | PGCIL | Satpura | 1 | 156 | Twin ACSR Moose | 50 | - | 2x125 | WRTS-1 | MPPTCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 813 | 815
|  |  | Khandwa | 1 | 352 | Quad AAAC Moose | 80 | - |  | WRTS-1 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 813 | 815
|  |  | Khandwa | 2 | 352 | Quad AAAC Moose | 80 | - |  | WRTS-1 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 813 | 815
|  |  | Bhilai | 1 | 230 | Twin ACSR Moose | - | - |  | WRTS-1 | CSPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 815
|  | Total |  |  |  |  | 210 |  | 250 |  |  |  | 0 | 1 | 0 | 0 | 0 | 2 | 818 | 820
134 | Sholapur-M | MSETCL | Sholapur -PG | 1 | 178 | Twin ACSR Moose | - | - | - | MSETCL | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 818 | 820
|  |  | Parli-M | 1 | 182 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 818 | 820
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 821 | 823
135 | Shujalpur | PGCIL | Bina-PG | 1 | 200 | Twin ACSR Moose | 50 | - | 1X63 + 1X125 | WRTS-2 | WRST-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 821 | 823
|  |  | Bina-PG | 2 | 200 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRST-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 821 | 823
|  |  | Nagda | 1 | 202 | Twin ACSR Moose | 63 | Yes |  | WRTS-2 | MPPTCL |  | 0 | 0 | 1 | 0 | 0 | 0 | 821 | 823
|  |  | Nagda | 2 | 152 | Twin ACSR Moose | 63 | Yes |  | WRTS-2 | MPPTCL |  | 0 | 0 | 1 | 0 | 0 | 0 | 821 | 823
|  |  | RAPP | 1 | 201 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 821 | 823
|  |  | RAPP | 2 | 201 | Twin ACSR Moose | 50 | - |  |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 821 | 823
|  | Total |  |  |  |  | 326 |  | 188 |  |  |  | 0 | 4 | 2 | 0 | 0 | 0 | 828 | 830
136 | Sipat | NTPC | Raipur | 1 | 149 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 830
|  |  | Raipur | 2 | 149 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 830
|  |  | Raipur | 3 | 149 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 830
|  |  | Ranchi | 1 | 405 | Twin ACSR Moose | 80 | - |  | WRTS-1/ERTS-1 | ERTS-1 |  | 0 | 0 | 0 | 0 | 0 | 1 | 828 | 830
|  |  | Ranchi | 2 | 405 | Twin ACSR Moose | 80 | - |  | WRTS-1/ERTS-1 | ERTS-1 |  | 0 | 0 | 0 | 0 | 0 | 1 | 828 | 830
|  |  | Korba-NTPC | 1 | 100 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 830
|  | Total |  |  |  |  | 160 |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 2 | 835 | 837
137 | SKS | SKS | Raigarh-PS(Kotra) | 1 | 28 | Twin ACSR Moose | - | - | 1x50 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 835 | 837
|  |  | Raigarh-PS(Kotra) | 2 | 28 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 835 | 837
|  | Total | [6 empty] | 50 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 840
138 | Soja | GETCO | Wanakbori | 1 | 95 | Twin ACSR Moose | - | - | 1X50 + 1X80 | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 840
|  |  | Dehgam | 1 | 41 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 840
|  |  | Zerda | 1 | 135 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 840
|  | Total |  |  |  |  | - |  | 130 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
139 | Solapur-NTPC | NTPC | Solapur-PG | 1 | 11 | Twin ACSR Moose | - | - | 1x80 | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
|  |  | Solapur-PG | 2 | 11 | Twin ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
|  |  | Solapur-PG | 3 | 12 | Quad ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
|  |  | Solapur-PG | 4 | 12 | Quad ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 844
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
140 | Solapur-PG | PGCIL | Solapur-NTPC | 1 | 11 | Twin ACSR Moose | - | - | 1X63 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Solapur-NTPC | 2 | 11 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Solapur-NTPC | 3 | 12 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Solapur-NTPC | 4 | 12 | Quad ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Kolhapur | 1 | 220 | Twin ACSR Moose | 50 | - |  | WRTMPL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Kolhapur | 2 | 220 | Twin ACSR Moose | 50 | - |  | WRTMPL | MSETCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Parli-PG | 1 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Parli-PG | 2 | 65 | Twin ACSR Moose | - | - |  | WRTMPL/WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
|  |  | Sholapur-M | 1 | 178 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 849
|  | Total |  |  |  |  | 100 |  | 63 |  |  |  | 0 | 2 | 0 | 0 | 0 | 0 | 857 | 859
141 | SSP | SSNL | Dhule | 1 | 236 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 859
|  |  | Dhule | 2 | 236 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 859
|  |  | Asoj | 1 | 83 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 859
|  |  | Rajgarh | 1 | 178 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 859
|  |  | Rajgarh | 2 | 178 | Twin ACSR Moose | - | - |  | MPPTCL | MPPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 859
|  |  | Kasor | 1 | 146 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 859
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 866
142 | Sugen | TPL | Uno-Sugen | 1 | 3 | Twin ACSR Moose | - | - | - | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 866
|  |  | Pirana-T | 1 | 212 | Twin ACSR Moose | - | - |  | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 866
|  |  | Pirana-T | 1 | 209 | Twin ACSR Moose | - | - |  | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 866
|  |  | Gandhar | 1 | 64 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 866
|  |  | Sugen | 1 | 3 | Twin ACSR Moose | - | - |  | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 866
|  |  | Vapi | 1 | 118 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 866
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 873
143 | Tamnar-PS | PGCIL | JPL_extn(Tamnar) | 1 | 10 | Twin ACSR Moose | - | - | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 873
|  |  | JPL_extn(Tamnar) | 2 | 10 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 873
|  |  | JPL_extn(Tamnar) | 3 | 10 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 873
|  |  | JPL_extn(Tamnar) | 3 | 10 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 873
|  |  | TRN | 1 | 15 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 873
|  |  | TRN | 2 | 15 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 871 | 873
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 878 | 880
144 | Taptithanda | MEGPTCL | Deepnagar | 1 | 203 | Twin ACSR Moose | - | - | - | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 878 | 880
|  |  | Ektuni (Aurangabad(3)) | 1 | 5 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 878 | 880
|  |  | Ektuni (Aurangabad(3)) | 2 | 5 | Twin ACSR Moose | - | - |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 878 | 880
|  |  | Aurangabad-M(Waluj) | 1 | 135 | Twin ACSR Moose | - | - |  | MSETCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 878 | 880
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 885
145 | Tarapur-3&4 | NPCIL | Padghe | 1 | 91 | Twin ACSR Moose | - | - | - | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 885
|  |  | Padghe | 2 | 91 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 885
|  |  | Boisar | 1 | 21 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 885
|  |  | Boisar | 2 | 21 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 885
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 890
146 | Tiroda | APML | Warora | 1 | 219 | Twin ACSR Moose | - | - | 2X80 | MEGPTCL | MEGPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 890
|  |  | Warora | 2 | 219 | Twin ACSR Moose | - | - |  | MEGPTCL | MEGPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 890
|  | Total |  |  |  |  | - |  | 160 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 891 | 893
147 | TRN | TRN | Tamnar-PS | 1 | 15 | Twin ACSR Moose | - | - | - | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 891 | 893
|  |  | Tamnar-PS | 2 | 15 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 891 | 893
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 896
148 | Ukai | TPL | Kosamba | 1 | 81 | Twin ACSR Moose | - | - | - | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 896
|  |  | Kosamba | 2 | 68 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 896
|  |  | Navsari | 1 | 83 | Twin ACSR Moose | - | - |  | GETCO | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 896
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 898 | 900
149 | Uno-Sugen | TPL | Pirana-T | 1 | 209 | Twin ACSR Moose | - | - | 1x80 | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 898 | 900
|  |  | Sugen | 1 | 3 | Twin ACSR Moose | - | - |  | TPL | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 898 | 900
|  | Total |  |  |  |  | - |  | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 903
150 | Vadinar | Essar | Hadala | 1 | 113 | Twin ACSR Moose | - | - | - | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 903
|  |  | Hadala | 2 | 113 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 903
|  |  | Bachau | 1 | 226 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 903
|  |  | Bachau | 2 | 226 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 903
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 908
151 | Vadodara-PS | PGCIL | Pirana-PG | 1 | 131 | Quad ACSR Moose | - | - | - | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 908
|  |  | Pirana-PG | 2 | 131 | Quad ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 908
|  |  | Asoj | 1 | 14 | Quad ACSR Moose | - | - |  | WRTS-2 | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 908
|  |  | Asoj | 2 | 14 | Quad ACSR Moose | - | - |  | WRTS-2 | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 908
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 911 | 913
152 | Vandana | Vandana Vidyut | Birsingpur | 1 | 215 | Twin ACSR Moose | 50 | - | - | WRTS-2 | MPPTCL |  | 0 | 1 | 0 | 0 | 0 | 0 | 911 | 913
|  |  | Korba-NTPC | 1 | 18 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 911 | 913
|  | Total |  |  |  |  | 50 |  | - |  |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 914 | 916
153 | Vapi | PGCIL | Boisar | 1 | 91 | Twin ACSR Moose | - | - | - | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 914 | 916
|  |  | Sugen | 1 | 118 | Twin ACSR Moose | - | - |  | WRTS-2 | TPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 914 | 916
|  |  | Kala | 1 | 49 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 914 | 916
|  |  | Kala | 2 | 52 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 914 | 916
|  |  | Kakrapar-3&4 | 1 | 117 | Twin ACSR Moose | - | - |  | WRTS-2 | NPCIL |  | 0 | 0 | 0 | 0 | 0 | 0 | 914 | 916
|  |  | Kakrapar-3&4 | 2 | 117 | Twin ACSR Moose | - | - |  | WRTS-2 | NPCIL |  | 0 | 0 | 0 | 0 | 0 | 0 | 914 | 916
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 923
154 | Varsana | GETCO | APL-Mundra | 1 | 84 | Twin ACSR Moose | - | - | 1X50 + 1X125 | GETCO | APL |  | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 923
|  |  | APL-Mundra | 2 | 84 | Twin ACSR Moose | - | - |  | GETCO | APL |  | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 923
|  |  | Bachau | 1 | 10 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 923
|  |  | Bachau | 2 | 10 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 923
|  |  | Hadala | 1 | 159 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 923
|  |  | Zerda(Kansari) | 1 | 258 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 923
|  | Total |  |  |  |  | - |  | 175 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 930
155 | Veloda | GETCO | Charnaka | 1 | 199 | Twin ACSR Moose | - | - | 1X125 | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 930
|  |  | Charnaka | 2 | 199 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 930
|  | Total |  |  |  |  | - | - | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 933
156 | Vindhyachal | NTPC | Jabalpur | 1 | 360 | Twin ACSR Moose | 63 | - | 1X63 + 1X50 | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 1 | 0 | 0 | 931 | 933
|  |  | Jabalpur | 2 | 360 | Twin ACSR Moose | 63 | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 1 | 0 | 0 | 931 | 933
|  |  | Jabalpur | 4 | 389 | Twin ACSR Moose | 63 | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 1 | 0 | 0 | 931 | 933
|  |  | Satna | 1 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Satna | 2 | 267 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Satna | 3 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Satna | 4 | 258 | Twin ACSR Moose | 50 | - |  | WRTS-2 | WRTS-2 |  | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Sasan | 3 | 20 | Twin ACSR Moose | 63 | Yes |  | WRTS-2 | SPL |  | 0 | 0 | 1 | 0 | 0 | 0 | 931 | 933
|  |  | Mahan | 1 | 41 | Twin ACSR Moose | 50 | - |  | WRTS-2 | Mahan |  | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Korba-NTPC | 2 | 289 | Twin ACSR Moose | 50 | - |  | WRTS-1 | NTPC |  | 0 | 1 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Vindhyachal-III | 1 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 933
|  |  | Vindhyachal-III | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 933
|  | Total |  |  |  |  | 552 |  | 113 |  |  |  | 0 | 6 | 1 | 3 | 0 | 0 | 944 | 946
157 | Vindhyachal-III | NTPC | Vindhyachal-V | 1 | 4 | Quad ACSR Moose | - | - | - | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 944 | 946
|  |  | Vindhyachal-V | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 944 | 946
|  |  | Vindhyachal | 1 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 944 | 946
|  |  | Vindhyachal | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 944 | 946
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 949 | 951
158 | Vindhyachal-IV | NTPC | Vindhyachal-V | 1 | 4 | Quad ACSR Moose | - | - | 1X80 | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 949 | 951
|  |  | Vindhyachal-V | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 949 | 951
|  |  | Vindhyachal-PS | 1 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 949 | 951
|  |  | Vindhyachal-PS | 2 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 949 | 951
|  | Total | [6 empty] | 80 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 956
159 | Vindhyachal-PS | PGCIL | Sasan | 1 | 8 | Twin ACSR Moose | - | - | 1X63 | WRTS-2 | SPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 956
|  |  | Sasan | 2 | 8 | Twin ACSR Moose | - | - |  | WRTS-2 | SPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 956
|  |  | Rihand | 1 | 35 | Quad Bersimis | - | - |  | WRTS-2/NRTS-1 | NRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 956
|  |  | Rihand | 2 | 28 | Quad Bersimis | - | - |  | WRTS-2/NRTS-1 | NRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 956
|  |  | Vindhyachal-IV | 1 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 956
|  |  | Vindhyachal-IV | 2 | 31 | Twin ACSR Moose | - | - |  | WRTS-2 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 956
|  | Total |  |  |  |  | - |  | 63 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 963
160 | Vindhyachal-V | NTPC | Vindhyachal-IV | 1 | 4 | Quad ACSR Moose | - | - | 1x125 | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 963
|  |  | Vindhyachal-IV | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 963
|  |  | Vindhyachal-III | 1 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 963
|  |  | Vindhyachal-III | 2 | 4 | Quad ACSR Moose | - | - |  | NTPC | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 963
|  | Total |  |  |  |  | - |  | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 966 | 968
161 | Wanakbori | GSECL | Asoj | 1 | 76 | Twin ACSR Moose | - | - | - | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 966 | 968
|  |  | Dehgam | 1 | 68 | Twin ACSR Moose | - | - |  | WRTS-2 | WRTS-2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 966 | 968
|  |  | Soja | 1 | 95 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 966 | 968
|  | Total |  |  |  |  | - |  | - |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 972
162 | Wardha | PGCIL | Parli-PG | 1 | 337 | Quad ACSR Moose | 63 | - | 1X50 | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 970 | 972
|  |  | Parli-PG | 2 | 337 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 970 | 972
|  |  | Akola | 1 | 162 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 972
|  |  | Akola | 2 | 162 | Twin ACSR Moose | - | - |  | WRTS-1 | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 972
|  |  | Mouda | 1 | 124 | Quad ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 972
|  |  | Mouda | 2 | 124 | Quad ACSR Moose | - | - |  | WRTS-1 | NTPC |  | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 972
|  |  | Warora | 1 | 76 | Twin ACSR Moose | - | - |  | WRTS-1 | MEGPTCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 972
|  |  | Koradi-II | 1 | 67 | Quad ACSR Moose | - | - |  | WRTS-1 | IEPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 972
|  |  | Raipur | 1 | 371 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 970 | 972
|  |  | Raipur | 2 | 371 | Quad ACSR Moose | 63 | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 1 | 0 | 0 | 970 | 972
|  | Total |  |  |  |  | 252 |  | 50 |  |  |  | 0 | 0 | 0 | 4 | 0 | 0 | 981 | 983
163 | Warora | MEGPTCL | Chandrapur-II | 1 | 45 | Twin ACSR Moose | - | - | 1x125 | MEGPTCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 983
|  |  | Chandrapur-II | 2 | 45 | Twin ACSR Moose | - | - |  | MEGPTCL | MSETCL |  | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 983
|  |  | IEPL | 1 | 150 | Twin ACSR Moose | - | - |  | WRTS-1 | IEPL |  | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 983
|  |  | Tiroda | 1 | 219 | Twin ACSR Moose | - | - |  | MEGPTCL | APML |  | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 983
|  |  | Tiroda | 2 | 219 | Twin ACSR Moose | - | - |  | MEGPTCL | APML |  | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 983
|  |  | Wardha | 1 | 76 | Twin ACSR Moose | - | - |  | WRTS-1 | WRTS-1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 981 | 983
|  | Total |  |  |  |  | - |  | 125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 990
164 | Zerda(Kansari) | GETCO | Bhinmal | 1 | 143 | Twin ACSR Moose | 50 | - | 1X50 + 1X125 | WRTS-2/NRTS-1 | NRTS-1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 988 | 990
|  |  | Kankroli | 1 | 234 | Twin ACSR Moose | 50 | - |  | WRTS-2/NRTS-1 | NRTS-1 |  | 0 | 1 | 0 | 0 | 0 | 0 | 988 | 990
|  |  | Varsana | 1 | 258 | Twin ACSR Moose | 63 | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 1 | 0 | 0 | 988 | 990
|  |  | APL-Mundra | 1 | 332 | Twin ACSR Moose | 63 | - |  | GETCO | APL |  | 0 | 0 | 0 | 1 | 0 | 0 | 988 | 990
|  |  | Ranchodpura | 1 | 140 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 990
|  |  | Ranchodpura | 2 | 140 | Twin ACSR Moose | - | - |  | WRTGPL | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 990
|  |  | Soja | 1 | 135 | Twin ACSR Moose | - | - |  | GETCO | GETCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 990
|  | Total |  |  |  |  | 226 |  | 175 |  |  |  | 0 | 2 | 0 | 2 | 0 | 0 | 996 | 998
[13 empty] | 42 | 246 | 18 | 74 | 10 | 18
[13 empty] | 2100 | 12300 | 1134 | 4662 | 800 | 1440

## 1200kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Km | Conductor Type | End1 LR |  | End2 LR
[9 empty] | MVAR | S/W | MVAR | S/W
1 | Bina-NTS | Bina-NTS | 1 | PGCIL | PGCIL | PGCIL | 1.9* | Octa Bersimis | - | - | - | -

## 1200kV ICTs
Sl No | Sub-Station | ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | Bina-NTS | 1 | 1000 | 1200/400 | PGCIL | - | -
2 | Bina-NTS | 2 | 1000 | 1200/400 | PGCIL | - | -

## 765 ICTs
Sl No | Sub-Station | Ckt ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | Akola(2) | 1 | 1500 | 765/400 | MEGPTCL | 12 | 11 |  | 0
2 | Aurangabad-PG | 1 | 1500 | 765/400 | PGCIL | 12 | 14 |  | 0
3 | Aurangabad-PG | 2 | 1500 | 765/400 | PGCIL | 12 | 14 |  | 1
4 | Bhopal-BDTCL | 1 | 1500 | 765/400 | BDTCL | 12 | 11 |  | 0
5 | Bhopal-BDTCL | 2 | 1500 | 765/400 | BDTCL | 12 | 11 |  | 1
6 | Bilaspur | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
7 | Bilaspur | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
8 | Bilaspur | 3 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
9 | Bina-PG | 1 | 1000 | 765/400 | PGCIL | 11 | 11 | MP | 0
10 | Bina-PG | 2 | 1000 | 765/400 | PGCIL | 11 | 11 | MP | 1
11 | Champa | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
12 | Champa | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
13 | Champa | 3 | 1500 | 765/400 | PGCIL | 12 | 12
14 | Champa | 4 | 1500 | 765/400 | PGCIL | 12 | 12
15 | Champa | 5 | 1500 | 765/400 | PGCIL | 12 | 12
16 | Champa | 6 | 1500 | 765/400 | PGCIL | 12 | 12
17 | Dharamjaygarh | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
18 | Dharamjaygarh | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
19 | Dhule-BDTCL | 1 | 1500 | 765/400 | BDTCL | 12 | 13 |  | 0
20 | Dhule-BDTCL | 2 | 1500 | 765/400 | BDTCL | 12 | 13 |  | 1
21 | Ektuni (Aurangabad(3)) | 1 | 1500 | 765/400 | MEGPTCL | 12 | 12 |  | 0
22 | Ektuni (Aurangabad(3)) | 2 | 1500 | 765/400 | MEGPTCL | 12 | 12
23 | Gwalior | 1 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 0
24 | Gwalior | 2 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 1
25 | Indore-PG | 1 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 0
26 | Indore-PG | 2 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 1
27 | Jabalpur-PS | 1 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 0
28 | Jabalpur-PS | 2 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 1
29 | Koradi(III) | 1 | 1500 | 765/400 | MEGPTCL | 12 | 11 |  | 0
30 | Koradi(III) | 2 | 1500 | 765/400 | MEGPTCL | 12 | 11 |  | 1
31 | Pune-PG(Shikrapur) | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
32 | Pune-PG(Shikrapur) | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
33 | Raigarh-PS(Kotra) | 1 | 1500 | 765/400 | PGCIL | 12 | 13 |  | 0
34 | Raigarh-PS(Kotra) | 2 | 1500 | 765/400 | PGCIL | 12 | 13 |  | 1
35 | Raigarh-PS(Kotra) | 3 | 1500 | 765/400 | PGCIL | 12 | 13 |  | 1
36 | Raigarh-PS(Kotra) | 4 | 1500 | 765/400 | PGCIL | 12 | 13 |  | 1
37 | Raipur-PS(Durg) | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
38 | Raipur-PS(Durg) | 2 | 1500 | 765/400 | PGCIL | 12 | 12
39 | Sasan | 1 | 1000 | 765/400 | SPL | 11 | 11 | MP | 0
40 | Sasan | 2 | 1000 | 765/400 | SPL | 11 | 11 | MP | 1
41 | Satna | 1 | 1000 | 765/400 | PGCIL | 11 | 12 | MP | 0
42 | Satna | 2 | 1000 | 765/400 | PGCIL | 11 | 12 | MP | 1
43 | Seoni | 1 | 1500 | 765/400 | PGCIL | 12 | 6 | MP | 0
44 | Seoni | 2 | 1500 | 765/400 | PGCIL | 12 | 6 | MP | 1
45 | Seoni | 3 | 1500 | 765/400 | PGCIL | 12 | 6 | MP | 1
46 | Sipat | 1 | 1000 | 765/400 | NTPC | 9B | 9B |  | 0
47 | Sipat | 2 | 1000 | 765/400 | NTPC | 9B | 9B |  | 1
48 | Solapur | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
49 | Solapur | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
50 | Tamnar | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
51 | Tamnar | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
52 | Tamnar | 3 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
53 | Tamnar | 4 | 1500 | 765/400 | PGCIL | 12 | 12
54 | Tiroda | 1 | 1500 | 765/400 | APML | 12 | 11 |  | 0
55 | Vadodora-PS | 1 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 0
56 | Vadodora-PS | 2 | 1500 | 765/400 | PGCIL | 12 | 12 |  | 1
57 | Vindhyachal-PS | 1 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 0
58 | Vindhyachal-PS | 2 | 1500 | 765/400 | PGCIL | 12 | 12 | MP | 1
59 | Vindhyachal-PS | 3 | 1500 | 765/400 | PGCIL | 12 | 12
60 | Wardha | 1 | 1500 | 765/400 | PGCIL | 12 | 13 |  | 0
61 | Wardha | 2 | 1500 | 765/400 | PGCIL | 12 | 13 |  | 1
62 | Wardha | 3 | 1500 | 765/400 | PGCIL | 12 | 13 |  | 1
|  | Total | 89000

## 400 ICTs
Sl No | Sub-Station | ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | ACBIL | 1 | 200 | 400/132 | ACBIL | 9 | 9 |  | 0
2 | Akola(2) | 1 | 315 | 400/220 | MEGPTCL | 9b | 8
3 | Akola(2) | 2 | 315 | 400/220 | MEGPTCL | 9b | 8 |  | 0
4 | Alkud | 1 | 500 | 400/220 | MSETCL | 9b | 9b |  | 0
5 | Amreli | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
6 | Amreli | 2 | 315 | 400/220 | GETCO | 9b | 9 |  | 1
7 | Amreli | 3 | 315 | 400/220 | GETCO | 9b | 9 | MP | 1
8 | APL-Mundra | 1 | 315 | 400/220 | APL | 9b | 9 |  | 0
9 | APL-Mundra | 2 | 315 | 400/220 | APL | 9b | 9 |  | 1
10 | Asoj | 1 | 500 | 400/220 | GETCO | 9 | 12 |  | 0
11 | Asoj | 2 | 500 | 400/220 | GETCO | 9 | 12 |  | 1
12 | Asoj | 3 | 315 | 400/220 | GETCO | 9b | 12 |  | 1
13 | Asoj | 4 | 315 | 400/220 | GETCO | 9b | 12 |  | 1
14 | Astha | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
15 | Astha | 2 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 1
16 | Aurangabad-M(Waluj) | 3 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
17 | Aurangabad-M(Waluj) | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
18 | Aurangabad-M(Waluj) | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
19 | Aurangabad-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 0
20 | Aurangabad-PG | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
21 | Bableshwar | 4 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
22 | Bableshwar | 3 | 500 | 400/220 | MSETCL | 9 | 9 |  | 1
23 | Bableshwar | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
24 | Bableshwar | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
25 | Bachau | 1 | 315 | 400/220 | PGCIL | 9b | 7 |  | 0
26 | Bachau | 2 | 315 | 400/220 | PGCIL | 9b | 7 |  | 1
27 | Balco | 1 | 315 | 400/220 | BALCO | 9b | 9 |  | 0
28 | Balco | 2 | 315 | 400/220 | BALCO | 9b | 9 |  | 1
29 | Balco | 3 | 315 | 400/220 | BALCO | 9b | 9 |  | 1
30 | Betul | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
31 | Betul | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
32 | Bhadrawati | 1 | 250 | 400/220 | PGCIL | 9b | 9b |  | 0
33 | Bhatapara | 1 | 315 | 400/220 | PGCIL | 9b | 9b | MP | 0
34 | Bhatapara | 2 | 315 | 400/220 | PGCIL | 9b | 9b | MP | 1
35 | Bhilai | 1 | 315 | 400/220 | CSPTCL | 9b | 9 | MP | 0
36 | Bhilai | 2 | 315 | 400/220 | CSPTCL | 9b | 13 |  | 1
37 | Bhilai | 3 | 315 | 400/220 | CSPTCL | 9b | 13 | MP | 1
38 | Bhopal-MP | 1 | 315 | 400/220 | MPPTCL | 9b | 9 | MP | 0
39 | Bhopal-MP | 2 | 315 | 400/220 | MPPTCL | 9b | 9 | MP | 1
40 | Bhopal-MP | 3 | 315 | 400/220 | MPPTCL | 9b | 9 | MP | 1
41 | Bhusawal (Khadka) | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 0
42 | Bhusawal (Khadka) | 2 | 200 | 400/132 | MSETCL | 9b | 9
43 | Bhusawal (Khadka) | 3 | 200 | 400/132 | MSETCL | 9b | 9
44 | Bina-MP | 1 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 0
45 | Bina-MP | 2 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 1
46 | Bina-MP | 3 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 1
47 | Bina-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
48 | Birsingpur | 1 | 500 | 400/220 | MPPGCL | 9 | 11 |  | 0
49 | Boisar | 3 | 500 | 400/220 | PGCIL | 9 | 9 |  | 0
50 | Boisar | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
51 | Boisar | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
52 | Chakan | 1 | 315 | 400/220 | MSETCL | 9b | 11 |  | 0
53 | Chakan | 2 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
54 | Chandrapur | 1 | 315 | 400/220 | MSETCL | 9b | 9 | MP | 0
55 | Chandrapur | 2 | 315 | 400/220 | MSETCL | 9b | 9 | MP | 1
56 | Charnaka | 1 | 315 | 400/220 | GETCO | 9b | 9
57 | Charnaka | 2 | 315 | 400/220 | GETCO | 9b | 9
58 | Charnaka | 3 | 315 | 400/220 | GETCO | 9b | 9
59 | Chhegaon | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
60 | Chorania | 1 | 500 | 400/220 | GETCO | 9 | 9 |  | 0
61 | Chorania | 2 | 500 | 400/220 | GETCO | 9 | 9 |  | 1
62 | Chorania | 3 | 500 | 400/220 | GETCO | 9 | 9
63 | Damoh | 1 | 315 | 400/220 | PGCIL | 9b | 11
64 | Damoh | 2 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
65 | Damoh | 3 | 500 | 400/220 | PGCIL | 9b | 11 |  | 1
66 | Deepnagar | 1 | 500 | 400/220 | MSETCL | 9 | 10 |  | 0
67 | Deepnagar | 2 | 500 | 400/220 | MSETCL | 9 | 10 |  | 1
68 | Dehgam | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 0
69 | Dehgam | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
70 | Dhule-MS | 3 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
71 | Dhule-MS | 1 | 315 | 400/220 | MSETCL | 9b | 13 | MP | 1
72 | Dhule-MS | 2 | 315 | 400/220 | MSETCL | 9b | 13 | MP | 1
73 | Gandhar | 1 | 500 | 400/220 | NTPC | 9b | 10 | MP | 0
74 | Gandhar | 2 | 500 | 400/220 | NTPC | 9b | 10 |  | 1
75 | GPEC | 1 | 500 | 400/220 | GSECL | 9 | 11 |  | 0
76 | Gwalior | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
77 | Gwalior | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
78 | Gwalior | 3 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
79 | Hadala | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
80 | Hadala | 2 | 315 | 400/220 | GETCO | 9b | 9 | MP | 1
81 | Hadala | 3 | 315 | 400/220 | GETCO | 9b | 9 | MP | 1
82 | Hazira | 1 | 500 | 400/220 | ESSAR | 9 | 8 | MP | 0
83 | Hazira | 2 | 500 | 400/220 | ESSAR | 9 | 8 | MP | 1
84 | Hazira | 3 | 500 | 400/220 | ESSAR | 9 | 8 | MP | 1
85 | Indore-MP | 1 | 315 | 400/220 | MPPTCL | 9b | 13 | MP | 0
86 | Indore-MP | 2 | 315 | 400/220 | MPPTCL | 9b | 13 | MP | 1
87 | Indore-MP | 3 | 315 | 400/220 | MPPTCL | 9b | 13 |  | 1
88 | Indore-MP | 4 | 315 | 400/220 | MPPTCL | 9b | 13 |  | 1
89 | Itarsi | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
90 | Itarsi | 2 | 500 | 400/220 | PGCIL | 9b | 9b
91 | Jabalpur | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
92 | Jabalpur | 2 | 315 | 400/220 | PGCIL | 9b | 11 |  | 1
93 | Jagdalpur | 1 | 315 | 400/220 | CSPTCL | 9b | 9b
94 | Jejuri | 1 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
95 | Jejuri | 2 | 500 | 400/220 | MSETCL | 9 | 9 |  | 1
96 | Jetpur | 4 | 500 | 400/220 | GETCO | 9 | 9b |  | 0
97 | Jetpur | 1 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
98 | Jetpur | 2 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
99 | Jetpur | 3 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
100 | JPL | 1 | 315 | 400/220 | JPL | 9b | 9 |  | 0
101 | JPL | 2 | 315 | 400/220 | JPL | 9b | 9 |  | 1
102 | Julwania | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
103 | Julwania | 2 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 1
104 | Kala | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
105 | Kala | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
106 | Kalwa | 2 | 600 | 400/220 | MSETCL | 9B | 11 |  | 0
107 | Kalwa | 1 | 500 | 400/220 | MSETCL | 9B | 11 |  | 1
108 | Kalwa | 3 | 500 | 400/220 | MSETCL | 9 | 11 |  | 1
109 | Karad | 1 | 315 | 400/220 | MSETCL | 9b | 8 | MP | 0
110 | Karad | 2 | 315 | 400/220 | MSETCL | 9b | 8 | MP | 1
111 | Karad | 3 | 315 | 400/220 | MSETCL | 9b | 8 | MP | 1
112 | Kasor | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
113 | Kasor | 2 | 315 | 400/220 | GETCO | 9b | 9 |  | 1
114 | Kasor | 3 | 315 | 400/221 | GETCO | 9b | 9
115 | Katni | 1 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 0
116 | Katni | 2 | 315 | 400/220 | MPPTCL | 9b | 9 |  | 1
117 | Khandwa | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
118 | Khandwa | 2 | 315 | 400/220 | PGCIL | 9b | 11 |  | 1
119 | Khaparkheda | 1 | 500 | 400/220 | MSETCL | 9 | 7 |  | 0
120 | Khaparkheda | 2 | 500 | 400/220 | MSETCL | 9 | 7 |  | 1
121 | Kharghar | 2 | 500 | 400/220 | MSETCL | 9 | 11 |  | 0
122 | Kharghar | 1 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
123 | Kharghar | 3 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
124 | Kolhapur | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 0
125 | Kolhapur | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
126 | Kolhapur | 3 | 315 | 400/220 | MSETCL | 9b | 9
127 | Koradi | 1 | 315 | 400/220 | MSETCL | 9b | 7
128 | Koradi | 2 | 315 | 400/220 | MSETCL | 9b | 7 |  | 0
129 | Koradi-II | 1 | 500 | 400/220 | MSETCL | 9 | 7 |  | 0
130 | Koradi-II | 2 | 500 | 400/220 | MSETCL | 9 | 7 |  | 1
131 | Korba (W) | 1 | 500 | 400/220 | CSPGCL | 9B | 12 |  | 0
132 | Kosamba | 1 | 315 | 400/220 | GETCO | 9b | 8 |  | 0
133 | Kosamba | 2 | 315 | 400/220 | GETCO | 9b | 8 |  | 1
134 | Kosamba | 3 | 315 | 400/220 | GETCO | 9b | 8
135 | Kosamba | 4 | 500 | 400/220 | GETCO | 9b | 8
136 | Lonikhand | 1 | 315 | 400/220 | MSETCL | 9b | 13 |  | 0
137 | Lonikhand | 2 | 315 | 400/220 | MSETCL | 9b | 13 |  | 1
138 | Lonikhand | 3 | 315 | 400/220 | MSETCL | 9b | 13 | MP | 1
139 | Lonikhand-II | 1 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
140 | Lonikhand-II | 2 | 500 | 400/220 | MSETCL | 9 | 9 |  | 1
141 | Magarawada | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
142 | Magarawada | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
143 | Malwa | 1 | 315 | 400/220 | MPPTCL | 9b | 9b |  | 0
144 | Malwa | 2 | 315 | 400/220 | MPPTCL | 9b | 9b
145 | Mansar | 1 | 315 | 400/220 | GETCO | 9b | 7 |  | 0
146 | Mansar | 2 | 315 | 400/220 | GETCO | 9b | 7 |  | 1
147 | Mapusa | 1 | 315 | 400/220 | PGCIL | 9b | 10 |  | 0
148 | Mapusa | 2 | 315 | 400/220 | PGCIL | 9b | 10 | MP | 1
149 | Mapusa | 3 | 315 | 400/220 | PGCIL | 9b | 10 | MP | 1
150 | Marwa | 1 | 315 | 400/220 | CSEPTCL | 9b | 9b | MP | 0
151 | Mouda | 1 | 200 | 400/132 | NTPC | 9 | 9 |  | 0
152 | Mouda | 2 | 200 | 400/132 | NTPC | 9 | 9 |  | 1
153 | Nagda | 1 | 315 | 400/220 | MPPTCL | 9b | 11 |  | 0
154 | Nagda | 2 | 315 | 400/220 | MPPTCL | 9b | 11 |  | 1
155 | Nagda | 3 | 315 | 400/220 | MPPTCL | 9b | 11 |  | 1
156 | Nagda | 4 | 315 | 400/220 | MPPTCL | 9b | 11
157 | Nagothane | 3 | 500 | 400/220 | MSETCL | 9 | 8 |  | 0
158 | Nagothane | 1 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
159 | Nagothane | 2 | 315 | 400/220 | MSETCL | 9b | 9 |  | 1
160 | Nanded | 1 | 500 | 400/220 | MSETCL | 9b | 9b |  | 0
161 | Nanded | 2 | 500 | 400/220 | MSETCL | 9b | 9b |  | 1
162 | Navsari | 3 | 500 | 400/220 | PGCIL | 9 | 9 |  | 0
163 | Navsari | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
164 | Navsari | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
165 | New koyna | 2 | 500 | 400/220 | MSETCL | 9 | 11 |  | 0
166 | New koyna | 1 | 315 | 400/220 | MSETCL | 9b | 11 |  | 1
167 | Nicol-II | 1 | 315 | 400/132 | TPL | 9b | 9b |  | 0
168 | Nicol-II | 2 | 315 | 400/132 | TPL | 9b | 9b |  | 1
169 | Nicol-II | 3 | 315 | 400/132 | TPL | 9b | 9b |  | 1
170 | NSPCL | 1 | 315 | 400/220 | NSPCL | 9b | 8 |  | 0
171 | NSPCL | 2 | 315 | 400/220 | NSPCL | 9b | 8 | MP | 1
172 | Padghe | 4 | 600 | 400/220 | MSETCL | 9 | 8 | MP | 0
173 | Padghe | 1 | 315 | 400/220 | MSETCL | 9b | 8 |  | 1
174 | Padghe | 2 | 315 | 400/220 | MSETCL | 9b | 8 |  | 1
175 | Padghe | 3 | 315 | 400/220 | MSETCL | 9b | 8 |  | 1
176 | Parli-M | 3 | 500 | 400/220 | MSETCL | 9 | 12 |  | 0
177 | Parli-M | 1 | 315 | 400/220 | MSETCL | 9b | 12 |  | 1
178 | Parli-M | 2 | 315 | 400/220 | MSETCL | 9b | 12 |  | 1
179 | Pirana-PG | 1 | 315 | 400/220 | PGCIL | 9b | 10 |  | 0
180 | Pirana-PG | 2 | 315 | 400/220 | PGCIL | 9b | 10
181 | Pirana-T | 1 | 315 | 400/132 | TPL | 9 | 9
182 | Pirana-T | 2 | 315 | 400/132 | TPL | 9 | 9 |  | 0
183 | Pirana-T | 3 | 315 | 400/132 | TPL | 9 | 9 |  | 1
184 | Pirana-T | 4 | 315 | 400/132 | TPL | 9 | 9 |  | 1
185 | Pithampur | 1 | 315 | 400/220 | MPPTCL | 9b | 9b | MP | 0
186 | Pithampur | 2 | 315 | 400/220 | MPPTCL | 9b | 9b | MP | 1
187 | Pune-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 0
188 | Pune-PG | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
189 | Pune-PG | 3 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
190 | Raigarh | 1 | 315 | 400/220 | PGCIL | 9b | 13 |  | 0
191 | Raigarh | 2 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 1
192 | Raipur | 1 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 0
193 | Raipur | 2 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 1
194 | Raipur | 3 | 315 | 400/220 | PGCIL | 9b | 13 | MP | 1
195 | Raita | 1 | 315 | 400/220 | CSPTCL | 9b | 9 |  | 0
196 | Raita | 2 | 315 | 400/220 | CSPTCL | 9b | 9 |  | 1
197 | Rajgarh | 1 | 315 | 400/220 | PGCIL | 9b | 11 |  | 0
198 | Rajgarh | 2 | 315 | 400/220 | PGCIL | 9b | 11 |  | 1
199 | Ranchodpura | 1 | 315 | 400/220 | GETCO | 9b | 9b |  | 0
200 | Ranchodpura | 2 | 315 | 400/220 | GETCO | 9b | 9b |  | 1
201 | Ranchodpura | 3 | 315 | 400/220 | GETCO | 9b | 9b | MP | 1
202 | Ranchodpura | 4 | 315 | 400/220 | GETCO | 9b | 9b
203 | Satna | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
204 | Satna | 2 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
205 | Satna | 3 | 315 | 400/220 | PGCIL | 9b | 9b |  | 1
206 | Satpura | 1 | 500 | 400/220 | MPPGCL | 9 | 10 |  | 0
207 | Seoni | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 0
208 | Seoni | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
209 | Sholapur-MS | 1 | 500 | 400/220 | MSETCL | 9 | 11 |  | 0
210 | Sholapur-MS | 2 | 500 | 400/220 | MSETCL | 9 | 11 |  | 1
211 | Shujalpur | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
212 | Shujalpur | 2 | 315 | 400/220 | PGCIL | 9b | 9b
213 | Soja | 1 | 500 | 400/220 | GETCO | 9 | 11 |  | 0
214 | Soja | 2 | 500 | 400/220 | GETCO | 9 | 11 |  | 1
215 | Soja | 3 | 500 | 400/220 | GETCO | 9 | 11 |  | 1
216 | Solapur-NTPC | 1 | 200 | 400/132 | NTPC | 9b | 9
217 | Solapur-NTPC | 2 | 200 | 400/132 | NTPC | 9b | 9 |  | 0
218 | Solapur-PG | 3 | 500 | 400/220 | PGCIL | 9 | 9 |  | 0
219 | Solapur-PG | 1 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
220 | Solapur-PG | 2 | 315 | 400/220 | PGCIL | 9b | 9 |  | 1
221 | SSP | 1 | 315 | 400/220 | SSNL | 9b | 9b |  | 0
222 | SSP | 2 | 315 | 400/220 | SSNL | 9b | 9b
223 | Sugen | 1 | 315 | 400/220 | TPL | 9b | 1 |  | 0
224 | Sugen | 2 | 315 | 400/220 | TPL | 9b | 1
225 | Sugen | 3 | 315 | 400/220 | TPL | 9b | 1
226 | Taptithanda | 1 | 500 | 400/220 | MSETCL | 9 | 9 |  | 0
227 | Ukai | 1 | 315 | 400/220 | GETCO | 9b | 9 |  | 0
228 | Vadodara-PS | 1 | 500 | 400/220 | PGCIL | 9b | 9b |  | 0
229 | Vadodara-PS | 2 | 500 | 400/220 | PGCIL | 9b | 9b |  | 1
230 | Vapi | 1 | 315 | 400/220 | PGCIL | 9b | 12 |  | 0
231 | Vapi | 2 | 315 | 400/220 | PGCIL | 9b | 12
232 | Vapi | 3 | 315 | 400/220 | PGCIL | 9b | 12 |  | 1
233 | Varsana | 1 | 315 | 400/220 | GETCO | 9b | 5
234 | Varsana | 2 | 315 | 400/220 | GETCO | 9b | 5
235 | Varsana | 3 | 315 | 400/220 | GETCO | 9b | 5 |  | 0
236 | Varsana | 4 | 315 | 400/220 | GETCO | 9b | 5 |  | #REF!
237 | Veloda | 1 | 500 | 400/220 | GETCO | 9b | 9b |  | 0
238 | Wanakbori | 1 | 315 | 400/220 | GSECL | 9b | 9 |  | 0
239 | Wardha | 1 | 315 | 400/220 | PGCIL | 9b | 9b |  | 0
240 | Wardha | 2 | 315 | 400/220 | PGCIL | 9b | 9b
241 | Warora | 1 | 500 | 400/220 | MEGPTCL | 9 | 9
242 | Warora | 2 | 500 | 400/220 | MEGPTCL | 9 | 9
243 | Zerda(Kansari) | 1 | 315 | 400/220 | PGCIL | 9b | 11
244 | Zerda(Kansari) | 2 | 315 | 400/220 | PGCIL | 9b | 11
245 | Zerda(Kansari) | 3 | 315 | 400/220 | PGCIL | 9b | 11
|  | Total | 87050

## 765 SC MVA
Sl. No | BUS | kV | Three Phase Fault
|  |  | Three phase fault current (kA) | Three phase fault MVA
1 | Akola(2) | 765 | 12.9125 | 17108.8043
2 | APML Tirora | 765 | 14.2329 | 18858.3078
3 | Aurangabad-PG | 765 | 25.739 | 34103.6602
4 | Bhopal-BDTCL | 765 | 15.9031 | 21071.2894
5 | Bilaspur-PS | 765 | 31.0534 | 41145.1339
6 | Bina-PG | 765 | 35.3244 | 46804.1235
7 | Champa-PS | 765 | 31.9655 | 42353.6482
8 | Dharamjaygarh | 765 | 38.8377 | 51459.1757
9 | Dhule-BDTCL | 765 | 14.0339 | 18594.6368
10 | Ektuni | 765 | 10.6374 | 14094.3423
11 | Gadarwada-NTPC | 765 | 15.8613 | 21015.9053
12 | Gwalior-PG | 765 | 31.8536 | 42205.3829
13 | Indore-PG | 765 | 17.9316 | 23759.0114
14 | Jabalpur-PS | 765 | 29.8069 | 39493.5464
15 | Koradi-3 | 765 | 14.294 | 18939.2641
16 | Pune GIS-PG | 765 | 10.5253 | 13945.812
17 | Raigarh-PS | 765 | 28.5136 | 37779.9497
18 | Raipur-PS | 765 | 30.3702 | 40239.9076
19 | Sasan-UMPP | 765 | 30.3372 | 40196.1833
20 | Satna-PG | 765 | 29.1409 | 38611.1097
21 | Seoni-PG | 765 | 23.781 | 31509.3494
22 | Sipat-NTPC | 765 | 29.9098 | 39629.8868
23 | Solapur-PG | 765 | 21.6451 | 28679.3246
24 | Tamnar-PS | 765 | 23.3544 | 30944.1129
25 | Vadodara-PS | 765 | 14.649 | 19409.632
26 | Vindhyachal-PS | 765 | 28.4633 | 37713.3032
27 | Wardha-PG | 765 | 35.1265 | 46541.91

## DD DNH ICTS
Sl No | Sub-Station | Ckt ID | MVA | Voltage Ratio | Owner | Normal Tap Position | Present Tap Position
1 | Khadoli | 1 | 160 | 220/66 | Electricity Dep of DNH | 9 | 9
2 | Khadoli | 2 | 160 | 220/66 | Electricity Dep of DNH | 9 | 9
3 | Kharadpada | 1 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
4 | Kharadpada | 2 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
5 | Kharadpada | 3 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
6 | Kharadpada | 4 | 100 | 220/66 | Electricity Dep of DNH | 9 | 9
7 | Magarwara | 1 | 50 | 220/66 | Electricity Dep of DD | 9 | 9
8 | Magarwara | 2 | 100 | 220/66 | Electricity Dep of DD | 9 | 9
9 | Magarwara | 3 | 100 | 220/66 | Electricity Dep of DD | 9 | 9
10 | Magarwara | 4 | 160 | 220/66 | Electricity Dep of DD | 9 | 9

## 220kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Length (in Km) | Conductor Type
1 | Anuppur | Kotmikala | 1 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
2 | Anuppur | Kotmikala | 2 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
3 | Auraiya | Malanpur | 1 | MPPTCL | UPPTCL | MPPTCL | 146 | Single Zebra
4 | Auraiya | Mehgaon | 1 | MPPTCL | UPPTCL | MPPTCL | 113 | Single Zebra
5 | Aurangabad-PG | Chitegoan | 1 | MSETCL | WRTS-1 | MSETCL | 34 | Single Zebra
6 | Aurangabad-PG | Chitegoan | 2 | MSETCL | WRTS-1 | MSETCL | 34 | Single Zebra
7 | Aurangabad-PG | Shendra | 1 | MSETCL | WRTS-1 | MSETCL | 11 | Single Zebra
8 | Aurangabad-PG | Shendra | 2 | MSETCL | WRTS-1 | MSETCL | 11 | Single Zebra
9 | Badod | Sakatpur | 1 | MPPTCL | MPPTCL | RSPTCL | 199 | Single Zebra
10 | Badod | Nepniya | 1 | MPPTCL | MPPTCL | RSPTCL | 62 | Single Zebra
11 | Belewadi | Mudshingi | 1 | MSETCL | 55 | Single Zebra | 55 | Single Zebra
12 | Betul | Betul-MP | 1 | MPPTCL |  |  | 31 | Single Zebra
13 | Betul | Betul-MP | 2 | MPPTCL |  |  | 31 | Single Zebra
14 | Bhanpura | Modak | 1 | MPPTCL | MPPTCL | MPPTCL | 63 | Single Zebra
15 | Bhatapara-PG | Bhatapara-CG | 1 | CSPTCL | WRTS-1 | CSPTCL | 7 | Single Zebra
16 | Bhatapara-PG | Suhela | 1 | CSPTCL | WRTS-1 | CSPTCL | 19 | Single Zebra
17 | Bhatapara-PG | Suhela | 2 | CSPTCL | WRTS-1 | CSPTCL | 19 | Single Zebra
18 | Bhatapara-PG | Suhela | 3 | CSPTCL | WRTS-1 | CSPTCL | 19 | Single Zebra
19 | Bhilad | Vapi-PG | 1 | GETCO | GETCO | WRTS-2 | 21 | Single Zebra
20 | Bhilad | Vapi-PG | 2 | GETCO | GETCO | WRTS-2 | 22 | Single Zebra
21 | Bhilad | Vapi-PG | 3 | GETCO | GETCO | WRTS-2 | 22 | Single Zebra
22 | Bhilai | Bhilai Steel Plant | 1 | CSPTCL |  |  | 10 | Single Zebra
23 | Bhilai | Bhilai Steel Plant | 2 | CSPTCL |  |  | 10 | Single Zebra
24 | Bina-MP | Bina-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
25 | Bina-MP | Mahalgaon | 1 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
26 | Bina-MP | Mahalgaon | 2 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
27 | Bina-PG | Shivpuri | 1 | MPPTCL | MPPTCL | MPPTCL | 169 | Single Zebra
28 | Boisar-PG | Vasai | 1 | MSETCL | WRTS-1 | MSETCL | 11 | Single Zebra
29 | Boisar-PG | Boisar-M | 1 | MSETCL | WRTS-1 | MSETCL | 53 | Single Zebra
30 | Boisar-PG | Boisar-M | 2 | MSETCL | WRTS-1 | MSETCL | 53 | Single Zebra
31 | Boisar-PG | Boisar-M | 3 | MSETCL |  |  | 53 | Single Zebra
32 | Damoh-MP | Damoh-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 8 | Single Zebra
33 | Damoh-MP | Damoh-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 9 | Single Zebra
34 | Damoh-PG | Sagar | 2 | MPPTCL | WRTS-2 | MPPTCL | 62 | Single Zebra
35 | Damoh-PG | Tikamgad | 1 | MPPTCL | WRTS-2 | MPPTCL | 151 | Single Zebra
36 | Dehgam | Ranasan | 1 | GETCO | WRTS-2 | GETCO | 20 | Single Zebra
37 | Dehgam | Ranasan | 2 | GETCO | WRTS-2 | GETCO | 20 | Single Zebra
38 | Dehgam | Khanpur | 1 | GETCO | WRTS-2 | GETCO | 12 | Single Zebra
39 | Dehgam | Khanpur | 2 | GETCO | WRTS-2 | GETCO | 12 | Single Zebra
40 | Gandhar | Haldarwa | 2 | WRTS-2 | NTPC | GETCO | 13 | Single Zebra
41 | Gandhar | Haldarwa | 1 | WRTS-2 | NTPC | GETCO | 13 | Single Zebra
42 | Gwalior | Malanpur | 1 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
43 | Gwalior | Malanpur | 2 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
44 | Gwalior | Mahalgaon | 1 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
45 | Gwalior | Mahalgaon | 2 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
46 | Gwalior | Gwalior-II | 1 | MPPTCL | WRTS-3 | MPPTCL | 3 | Single Zebra
47 | Gwalior | Gwalior-II | 2 | MPPTCL | WRTS-4 | MPPTCL | 3 | Single Zebra
48 | Halkarni | Tillari | 1 | MSETCL | MSETCL | MSETCL | 29 | Single Zebra
49 | Halvad | Bhimasar | 1 | GETCO | GETCO | GETCO | 150 | Single Zebra
50 | Halvad | Bhimasar | 2 | GETCO | GETCO | GETCO | 150 | Single Zebra
51 | Hamidwada | Talandge | 1 | MSETCL | 36 | Single Zebra | 36 | Single Zebra
52 | Hoshangabad | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 21 | Single Zebra
53 | Itarsi | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
54 | Jabalpur | Jabalpur-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
55 | Jabalpur | Jabalpur-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
56 | Kakrapar | Haldarwa | 1 | WRTS-2 | NPCIL | GETCO | 74 | Single Zebra
57 | Kakrapar | Haldarwa | 2 | WRTS-2 | NPCIL | GETCO | 74 | Single Zebra
58 | Kakrapar | Vav | 1 | WRTS-2 | NPCIL | GETCO | 43 | Single Zebra
59 | Kakrapar | Vav | 2 | WRTS-2 | NPCIL | GETCO | 43 | Single Zebra
60 | Kakrapar | Vapi-PG | 1 | WRTS-2 | NPCIL | WRTS-2 | 117 | Single Zebra
61 | Kakrapar | Vapi-PG | 2 | WRTS-2 | NPCIL | WRTS-2 | 117 | Single Zebra
62 | Kala | Kharadpada-PG | 1 | DNH | WRTS-2 | DNH | 30 | Single Zebra
63 | Kala | Kharadpada-PG | 2 | DNH | WRTS-2 | DNH | 30 | Single Zebra
64 | Kala | Khadoli | 1 | DNH | WRTS-2 | DNH | 8 | Single Zebra
65 | Kala | Khadoli | 2 | DNH | WRTS-2 | DNH | 8 | Single Zebra
66 | Katni | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 102 | Single Zebra
67 | Kawas | Haldarwa | 1 | WRTS-2 | NTPC | GETCO | 81 | Single Zebra
68 | Kawas | Haldarwa | 2 | WRTS-2 | NTPC | GETCO | 81 | Single Zebra
69 | Kawas | Navsari-PG | 1 | WRTS-2 | NTPC | WRTS-2 | 56 | Single Zebra
70 | Kawas | Navsari-PG | 2 | WRTS-2 | NTPC | WRTS-2 | 56 | Single Zebra
71 | Kawas | Vav | 1 | WRTS-2 | NTPC | GETCO | 37 | Single Zebra
72 | Kawas | Vav | 2 | WRTS-2 | NTPC | GETCO | 37 | Single Zebra
73 | Kawas | Ichchapur | 1 | GETCO | NTPC | GETCO | 3 | Single Zebra
74 | Kawas | Ichchapur | 2 | GETCO | NTPC | GETCO | 3 | Single Zebra
75 | Khandwa | Omkareswar | 1 | MPPTCL | WRTS-2 | MPPTCL | 98 | Single Zebra
76 | Kharadpada-PG | Kharadpada-DNH | 1 | DNH | WRTS-2 | DNH | 1 | Single Zebra
77 | Kharadpada-PG | Kharadpada-DNH | 2 | DNH | WRTS-2 | DNH | 1 | Single Zebra
78 | Kolhapur | Mumewadi | 1 | MSETCL | MSETCL | MSETCL | 52 | Single Zebra
79 | Kolhapur(Mudshingi) | Chikkodi | 1 | KPTCL/MSETCL | MSETCL | KPTCL | 155 | Single Zebra
80 | Kolhapur(Talandage) | Kolhapur(Mudshingi) | 1 | MSETCL | MSETCL | MSETCL | 5 | Single Zebra
81 | Kolhapur(Talandage) | Kolhapur(Mudshingi) | 2 | MSETCL | MSETCL | MSETCL | 5 | Single Zebra
82 | Kolhapur(Talandage) | Chikkodi | 1 | KPTCL/MSETCL | MSETCL | KPTCL | 150 | Single Zebra
83 | Korba East | Budhipadar | 2 | OPTCL | CSPTCL | OPTCL | 176 | Single Zebra
84 | Korba East | Budhipadar | 3 | OPTCL | CSPTCL | OPTCL | 176 | Single Zebra
85 | Korba East | Raigarh | 1 | WRTS-1 | CSPTCL | CSPTCL | 110 | Single Zebra
86 | Magarwada-PG | Magarwada-DD | 1 | DD | WRTS-2 | DD | 2 | Single Zebra
87 | Magarwada-PG | Magarwada-DD | 2 | DD | WRTS-2 | DD | 2 | Single Zebra
88 | Mahalaxmi (Konalkatta) | Amona | 1 | MSETCL | MSETCL | GED | 28 | Single Zebra
89 | Mahalaxmi (Konalkatta) | Halkarni | 1 | MSETCL |  |  | 38 | Single Zebra
90 | Mapusa | Amona | 1 | WRTS-1 | WRTS-1 | GED | 25 | Single Zebra
91 | Mapusa | Ponda | 1 | WRTS-1 | WRTS-1 | GED | 43 | Single Zebra
92 | Mapusa | Tivim | 1 | WRTS-1 | WRTS-1 | GED | 5 | Single Zebra
93 | Mapusa | Tivim | 2 | WRTS-1 | WRTS-1 | GED | 5 | Single Zebra
94 | Mehgaon | Malanpur | 1 | MPPTCL | MPPTCL | MPPTCL | 37 | Single Zebra
95 | Morbi | Hadala | 2 | GETCO | GETCO | GETCO | 59 | Single Zebra
96 | Morbi | Halvad | 1 | GETCO | GETCO | GETCO | 43 | Single Zebra
97 | Mumewadi | Halkarni | 1 | MSETCL | MSETCL | MSETCL | 49 | Single Zebra
98 | Mumewadi | Halkarni | 2 | MSETCL |  |  | 50 | Single Zebra
99 | Mumewadi | Belewadi | 1 | MSETCL | 6 | Single Zebra | 6 | Single Zebra
100 | Mumewadi | Hamidwada | 1 | MSETCL | 23 | Single Zebra | 23 | Single Zebra
101 | Nasik | Navsari | 1 | MSETCL | MSETCL | GETCO | 171 | Single Zebra
102 | Nasik | Navsari | 2 | MSETCL | MSETCL | GETCO | 171 | Single Zebra
103 | Navsari-PG | Navsari | 1 | WRTS-2 | WRTS-2 | WRTS-2 | 10 | Single Zebra
104 | Navsari-PG | Navsari | 2 | GETCO | WRTS-2 | GETCO | 10 | Single Zebra
105 | Nepniya | Bhanpura | 1 | MPPTCL | MPPTCL | MPPTCL | 51 | Single Zebra
106 | NSPCL | Bhilai Steel Plant | 1 | NSPCL |  |  | 3.4 | Single Zebra
107 | NSPCL | Bhilai Steel Plant | 2 | NSPCL |  |  | 3.4 | Single Zebra
108 | NSPCL | Bhilai Steel Plant | 3 | NSPCL |  |  | 4.15 | Single Zebra
109 | NSPCL | Bhilai Steel Plant | 4 | NSPCL |  |  | 4.15 | Single Zebra
110 | Pandurna | Kalmeshwar | 1 | MSETCL/MPPTCL | MPPTCL | MSETCL | 68 | Single Zebra
111 | Pithampura | Rajgarh-PG | 1 | MPPTCL | MPPTCL | WRTS-1 | 79 | Single Zebra
112 | Pithampura | Rajgarh-PG | 2 | MPPTCL | MPPTCL | WRTS-1 | 78 | Single Zebra
113 | Ponda | Ambewadi | 1 | GED/KPTCL | GED | KPTCL | 120 | Single Zebra
114 | Raigarh-CG | Raigarh-PG | 3 | CSPTCL | CSPTCL | OPTCL | 11 | Single Zebra
115 | Raigarh-PG | Bhudhipadar | 1 | CSPTCL |  |  | 26 | Single Zebra
116 | Raigarh-PG | Raigarh-CG | 1 | CSPTCL | WRTS-1 | CSPTCL | 15 | Single Zebra
117 | Raigarh-PG | Raigarh-CG | 2 | CSPTCL | WRTS-1 | CSPTCL | 15 | Single Zebra
118 | Rajgarh-PG | Rajgarh-MP | 1 | MPPTCL | WRTS-2 | MPPTCL | 13 | Single Zebra
119 | Rajgarh-PG | Dhar | 1 | MPPTCL | WRTS-2 | MPPTCL | 12 | Single Zebra
120 | Satna-MP | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
121 | Satna-MP | Satna-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
122 | Satna-PG | Maihar | 2 | MPPTCL | WRTS-2 | MPPTCL | 42 | Single Zebra
123 | Sayali | Khadoli | 1 | WRTS-2 | DNH | DNH | 12 | Single Zebra
124 | Seoni-PG | Seoni-MP | 1 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
125 | Seoni-PG | Seoni-MP | 2 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
126 | Seoni-PG | Chindwara | 1 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
127 | Seoni-PG | Chindwara | 2 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
128 | Shujalpur | Shujalpur-MP | 1 | MPPTCL | WRTS-2 | MPPTCL | 4 | Single Zebra
129 | Shujalpur | Shujalpur-MP | 2 | MPPTCL | WRTS-2 | MPPTCL | 4 | Single Zebra
130 | Solapur-PG | Kumbari | 1 | WRTS-1 | WRTS-1 | MSETCL | 7 | Single Zebra
131 | Solapur-PG | Kumbari | 2 | WRTS-1 | WRTS-1 | MSETCL | 7 | Single Zebra
132 | Solapur-PG | Jeur | 1 | WRTM/ MSETCL |  |  | 170 | Twin Moose
133 | Talegaon | Pune-PG | 1 | MSETCL | MSETCL | WRTS-1 | 4 | Single Zebra
134 | Talegaon | Pune-PG | 2 | MSETCL | MSETCL | WRTS-1 | 4 | Single Zebra
135 | Tarapur-1&2 | Vapi | 1 | WRTS-1 | NPCIL | GETCO | 117 | Single Zebra
136 | Tarapur-1&2 | Bhilad | 1 | WRTS-1 | NPCIL | GETCO | 62 | Single Zebra
137 | Tarapur-1&2 | Boisar-M | 1 | WRTS-1 | NPCIL | MSETCL | 20 | Single Zebra
138 | Tarapur-1&2 | Borivali | 1 | WRTS-1 | NPCIL | MSETCL | 96 | Single Zebra
139 | Tarapur-3&4 | Boisar-PG | 1 | WRTS-2 | NPCIL | WRTS-2 | 21 | Single Zebra
140 | Tarapur-3&4 | Tarapur-1&2 | 1 | WRTS-1 | NPCIL | NPCIL | 1 | Single Zebra
141 | Tillari | Amona | 1 | MSETCL | MSETCL | GED | 37 | Single Zebra
142 | Vapi-PG | Magarwada | 1 | WRTS-2 | WRTS-2 | DD | 26 | Single Zebra
143 | Vapi-PG | Magarwada | 2 | WRTS-2 | WRTS-2 | DD | 26 | Single Zebra
144 | Vapi-PG | Kharadpada-DNH | 1 | WRTS-2 | WRTS-2 | DNH | 30 | Single Zebra
145 | Vapi-PG | Kharadpada-DNH | 2 | WRTS-2 | WRTS-2 | DNH | 30 | Single Zebra
146 | Vapi-PG | Khadoli | 1 | WRTS-2 | WRTS-2 | DNH | 28 | Single Zebra
147 | Vapi-PG | Sayali | 1 | WRTS-2 | WRTS-2 | DNH | 19 | Single Zebra
148 | Wardha-PG | Wardha-M | 1 | MSETCL | WRTS-1 | MSETCL | 25 | Single Zebra
149 | Wardha-PG | Badnera | 1 | MSETCL | WRTS-1 | MSETCL | 95 | Single Zebra
150 | Wardha-PG | Pusad | 1 | MSETCL | WRTS-1 | MSETCL | 148 | Single Zebra
151 | Wardha-PG | Bhugaon | 1 | MSETCL | WRTS-1 | MSETCL | 20 | Single Zebra
152 | Xeldem | Ambewadi | 1 | GED/KPTCL | GED | KPTCL | 120 | Single Zebra
|  |  |  | Total |  | Sub-Total | 7258.1

## 132 kV lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Km | Conductor Type | End1 LR |  | End2 LR
[9 empty] | MVAR | S/W | MVAR | S/W
1 | Dharni | Nepanagar | 1 |  | MSETCL | MPPTCL | 60 |  | - | - | - | -

## RGMO FGMO_States
List of Generators Mandated for RGMO/FGMO by IEGC
Maharashtra
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | APL-Tiroda | 1 | 660 | Adani Power | Private
2 | APL-Tiroda | 2 | 660 | Adani Power | Private
3 | APL-Tiroda | 3 | 660 | Adani Power | Private
4 | APL-Tiroda | 4 | 660 | Adani Power | Private
5 | APL-Tiroda | 5 | 660 | Adani Power | Private
6 | Bhira (Hy) | 1 | 25 | Tata Hydro | Private
7 | Bhira (Hy) | 2 | 25 | Tata Hydro | Private
8 | Bhira (Hy) | 3 | 25 | Tata Hydro | Private
9 | Bhira (Hy) | 4 | 25 | Tata Hydro | Private
10 | Bhira (Hy) | 5 | 25 | Tata Hydro | Private
11 | Bhira (Hy) | 6 | 25 | Tata Hydro | Private
12 | Bhira PSS (Hy) | 1 | 150 | Tata Hydro | Private
13 | Bhira Tailrace (Hy) | 1 | 40 | MahaGenco | Private
14 | Bhira Tailrace (Hy) | 2 | 40 | MahaGenco | Private
15 | Bhusawal | 2 | 210 | MahaGenco | SS
16 | Bhusawal | 3 | 210 | MahaGenco | SS
17 | Bhusawal | 4 | 500 | MahaGenco | SS
18 | Bhusawal | 5 | 500 | MahaGenco | SS
19 | Chadrapur | 1 | 210 | MahaGenco | SS
20 | Chadrapur | 2 | 210 | MahaGenco | SS
21 | Chadrapur | 3 | 210 | MahaGenco | SS
22 | Chadrapur | 4 | 210 | MahaGenco | SS
23 | Chadrapur | 5 | 500 | MahaGenco | SS
24 | Chadrapur | 6 | 500 | MahaGenco | SS
25 | Chadrapur | 7 | 500 | MahaGenco | SS
26 | Chadrapur Ext | 1 | 500 | MahaGenco | SS
27 | Dhahanu | 1 | 250 | Reliance Energy | Private
28 | Dhahanu | 2 | 250 | Reliance Energy | Private
29 | Dhariwal | 1 | 300 | Dhariwal Infrastructure | Private
30 | Ghatghar (Hy) | 1 | 125 | MahaGenco | Private
31 | Ghatghar (Hy) | 2 | 125 | MahaGenco | Private
32 | IEPL | 1 | 270 | IEPL | Private
33 | Nandgaonpeth | 1 | 270 | Rattan India | Private
34 | Nandgaonpeth | 2 | 270 | Rattan India | Private
35 | Nandgaonpeth | 3 | 270 | Rattan India | Private
36 | Nandgaonpeth | 4 | 270 | Rattan India | Private
37 | Nandgaonpeth | 5 | 270 | Rattan India | Private
38 | JSW Ratnagiri | 1 | 300 | JSW | Private
39 | JSW Ratnagiri | 2 | 300 | JSW | Private
40 | JSW Ratnagiri | 3 | 300 | JSW | Private
41 | JSW Ratnagiri | 4 | 300 | JSW | Private
42 | Khaparkheda | 1 | 210 | MahaGenco | SS
43 | Khaparkheda | 2 | 210 | MahaGenco | SS
44 | Khaparkheda | 3 | 210 | MahaGenco | SS
45 | Khaparkheda | 4 | 210 | MahaGenco | SS
46 | Khaparkheda | 5 | 500 | MahaGenco | SS
47 | Koradi | 5 | 200 | MahaGenco | SS
48 | Koradi | 6 | 210 | MahaGenco | SS
49 | Koradi | 7 | 210 | MahaGenco | SS
50 | Koradi-II | 8 | 660 | MahaGenco | SS
51 | Koradi-II | 9 | 660 | MahaGenco | SS
52 | Koyna-I & II (Hy) | 1 | 70 | MahaGenco | SS
53 | Koyna-I & II (Hy) | 2 | 70 | MahaGenco | SS
54 | Koyna-I & II (Hy) | 3 | 70 | MahaGenco | SS
55 | Koyna-I & II (Hy) | 4 | 70 | MahaGenco | SS
56 | Koyna-I & II (Hy) | 5 | 80 | MahaGenco | SS
57 | Koyna-I & II (Hy) | 6 | 80 | MahaGenco | SS
58 | Koyna-I & II (Hy) | 7 | 80 | MahaGenco | SS
59 | Koyna-I & II (Hy) | 8 | 80 | MahaGenco | SS
60 | Koyna-III (Hy) | 9 | 80 | MahaGenco | SS
61 | Koyna-III (Hy) | 10 | 80 | MahaGenco | SS
62 | Koyna-III (Hy) | 11 | 80 | MahaGenco | SS
63 | Koyna-III (Hy) | 12 | 80 | MahaGenco | SS
64 | Koyna-IV (Hy) | 1 | 250 | MahaGenco | SS
65 | Koyna-IV (Hy) | 2 | 250 | MahaGenco | SS
66 | Koyna-IV (Hy) | 3 | 250 | MahaGenco | SS
67 | Koyna-IV (Hy) | 4 | 250 | MahaGenco | SS
68 | Nasik | 3 | 210 | MahaGenco | SS
69 | Nasik | 4 | 210 | MahaGenco | SS
70 | Nasik | 5 | 210 | MahaGenco | SS
71 | Nasik-Rattan India | 1 | 270 | Rattan India | Private
72 | Paras | 3 | 250 | MahaGenco | SS
73 | Paras | 4 | 250 | MahaGenco | SS
74 | Parli | 3 | 210 | MahaGenco | SS
75 | Parli | 4 | 210 | MahaGenco | SS
76 | Parli | 5 | 210 | MahaGenco | SS
77 | Parli | 6 | 250 | MahaGenco | SS
78 | Parli | 7 | 250 | MahaGenco | SS
79 | Pioneer Gas Pvt. Ltd.* | 1 | 126 | Pioneer | Private
80 | Pioneer Gas Pvt. Ltd.* | 2 | 262 | Pioneer | Private
81 | Tillari (Hy) | 1 | 60 | MahaGenco | SS
82 | Trombay | 8 | 250 | MahaGenco | SS
83 | Trombay | 5 | 500 | MahaGenco | SS
84 | Trombay | 6 | 500 | MahaGenco | SS
85 | Trombay-7A* | 1 | 120 | Tata Power | Private
86 | Trombay-7B* | 2 | 60 | Tata Power | Private
87 | Uran DPH* | 1 | 120 | MahaGenco | SS
88 | Uran DPH* | 2 | 120 | MahaGenco | SS
89 | Uran (G)* | 1 | 108 | MahaGenco | SS
90 | Uran (G)* | 2 | 108 | MahaGenco | SS
91 | Uran (G)* | 3 | 108 | MahaGenco | SS
92 | Uran (G)* | 4 | 108 | MahaGenco | SS
93 | Vaitharna (Hy) | 1 | 60 | MahaGenco | SS
94 | Vidarbha Industry | 1 | 300 | VIPCL | Private
95 | Vidarbha Industry | 2 | 300 | VIPCL | Private
|  | Total | 22750 |  |  | 290
* - Effective from 01.10.2017
Gujarat
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | APL_Mundra | 1 | 330 | APL | Private
2 | APL_Mundra | 2 | 330 | APL | Private
3 | APL_Mundra | 3 | 330 | APL | Private
4 | APL_Mundra | 4 | 330 | APL | Private
5 | APL_Mundra | 5 | 660 | APL | Private
6 | APL_Mundra | 6 | 660 | APL | Private
7 | APL_Mundra | 7 | 660 | APL | Private
8 | APL_Mundra | 8 | 660 | APL | Private
9 | APL_Mundra | 9 | 660 | APL | Private
10 | DGEN* | 1 | 400 | Torrent | Private
11 | DGEN* | 2 | 400 | Torrent | Private
12 | DGEN* | 3 | 400 | Torrent | Private
13 | Dhuvaran | 3 | 376 | GSECL | SS
14 | Dhuvaran* | 1 | 218.62 | GSECL | SS
15 | Essar* | 1 | 110 | Essar | Private
16 | Essar* | 2 | 110 | Essar | Private
17 | Essar* | 3 | 110 | Essar | Private
18 | Essar* | 4 | 185 | Essar | Private
19 | Gandhinagar | 3 | 210 | GSECL | SS
20 | Gandhinagar | 4 | 210 | GSECL | SS
21 | Gandhinagar | 5 | 210 | GSECL | SS
22 | GIPCL-I* | 4 | 49 | GIPCL | SS
23 | GIPCL-II* | 1 | 111 | GIPCL | SS
24 | GPEC* | 1 | 138 | GPEC | Private
25 | GPEC* | 2 | 138 | GPEC | Private
26 | GPEC* | 3 | 138 | GPEC | Private
27 | GPEC* | 4 | 241 | GPEC | Private
28 | GSEG Hazira* | 1 | 52 | GSEG | SS
29 | GSEG Hazira* | 2 | 52 | GSEG | SS
30 | GSEG Hazira* | 3 | 52.1 | GSEG | SS
31 | Hazira CPP Extn.* | 1 | 351 | Essar | Private
32 | Kadana (Hy) | 1 | 60 | GSECL | SS
33 | Kadana (Hy) | 2 | 60 | GSECL | SS
34 | Kadana (Hy) | 3 | 60 | GSECL | SS
35 | Kadana (Hy) | 4 | 60 | GSECL | SS
36 | Pipavav * | 1 | 351.43 | CCPP-GPCL & GSPC | Private
37 | Pipavav * | 2 | 351.43 | CCPP-GPCL & GSPC | Private
38 | Sikka | 4 | 250 | GSECL | SS
39 | Sugen* | 1 | 382.5 | Torrent | Private
40 | Sugen* | 2 | 382.5 | Torrent | Private
41 | Sugen* | 3 | 382.5 | Torrent | Private
42 | Ukai (Hy) | 1 | 75 | GSECL | SS
43 | Ukai (Hy) | 2 | 75 | GSECL | SS
44 | Ukai (Hy) | 3 | 75 | GSECL | SS
45 | Ukai (Hy) | 4 | 75 | GSECL | SS
46 | Ukai (Th) | 3 | 200 | GSECL | SS
47 | Ukai (Th) | 4 | 200 | GSECL | SS
48 | Ukai (Th) | 5 | 210 | GSECL | SS
49 | Ukai (Th) | 6 | 500 | GSECL | SS
50 | Uno sugen* | 1 | 382.5 | Torrent | Private
51 | Utran-II* | 1 | 229 | GSECL | SS
52 | Utran-II* | 2 | 146 | GSECL | SS
53 | Vadinar | 1 | 600 | Vadinar Power Company | Private
54 | Vadinar | 2 | 600 | Vadinar Power Company | Private
55 | Wanakbori | 1 | 210 | GSECL | SS
56 | Wanakbori | 2 | 210 | GSECL | SS
57 | Wanakbori | 3 | 210 | GSECL | SS
58 | Wanakbori | 4 | 210 | GSECL | SS
59 | Wanakbori | 5 | 210 | GSECL | SS
60 | Wanakbori | 6 | 210 | GSECL | SS
61 | Wanakbori | 7 | 210 | GSECL | SS
|  | Total | 16059.58
* - Effective from 01.10.2017
Madhya Pradesh
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Amarkantak | 5 | 210 | MPGCL | SS
2 | Bansagar Tons (Hy) | 1 | 105 | MPGCL | SS
3 | Bansagar Tons (Hy) | 2 | 105 | MPGCL | SS
4 | Bansagar Tons (Hy) | 3 | 105 | MPGCL | SS
5 | Bargi (Hy) | 1 | 50 | MPGCL | SS
6 | Bargi (Hy) | 2 | 50 | MPGCL | SS
7 | Indirasagar (Hy) | 1 | 125 | MPGCL | SS
8 | Indirasagar (Hy) | 2 | 125 | MPGCL | SS
9 | Indirasagar (Hy) | 3 | 125 | MPGCL | SS
10 | Indirasagar (Hy) | 4 | 125 | MPGCL | SS
11 | Indirasagar (Hy) | 5 | 125 | MPGCL | SS
12 | Indirasagar (Hy) | 6 | 125 | MPGCL | SS
13 | Indirasagar (Hy) | 7 | 125 | MPGCL | SS
14 | Indirasagar (Hy) | 8 | 125 | MPGCL | SS
15 | JP Bina | 1 | 250 | Jaypee Group | Private
16 | JP Bina | 2 | 250 | Jaypee Group | Private
17 | Omkareshwar (Hy) | 1 | 65 | MPGCL | SS
18 | Omkareshwar (Hy) | 2 | 65 | MPGCL | SS
19 | Omkareshwar (Hy) | 3 | 65 | MPGCL | SS
20 | Omkareshwar (Hy) | 4 | 65 | MPGCL | SS
21 | Omkareshwar (Hy) | 5 | 65 | MPGCL | SS
22 | Omkareshwar (Hy) | 6 | 65 | MPGCL | SS
23 | Omkareshwar (Hy) | 7 | 65 | MPGCL | SS
24 | Omkareshwar (Hy) | 8 | 65 | MPGCL | SS
25 | Pench (Hy) | 1 | 80 | MPGCL | SS
26 | Pench (Hy) | 2 | 80 | MPGCL | SS
27 | Sanjay Gandhi TPS | 1 | 210 | MPGCL | SS
28 | Sanjay Gandhi TPS | 2 | 210 | MPGCL | SS
29 | Sanjay Gandhi TPS | 3 | 210 | MPGCL | SS
30 | Sanjay Gandhi TPS | 4 | 210 | MPGCL | SS
31 | Sanjay Gandhi TPS-II | 5 | 500 | MPGCL | SS
32 | Satpura-II | 6 | 200 | MPGCL | SS
33 | Satpura-II | 7 | 210 | MPGCL | SS
34 | Satpura-III | 8 | 210 | MPGCL | SS
35 | Satpura-III | 9 | 210 | MPGCL | SS
36 | Satpura-IV | 10 | 250 | MPGCL | SS
37 | Satpura-IV | 11 | 250 | MPGCL | SS
38 | Singhaji | 1 | 600 | MPGCL | SS
39 | Singhaji | 2 | 600 | MPGCL | SS
|  | Total | 6675
Chhattisgarh
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Hasdeo Bango (Hy) | 1 | 40 | CSPGCL | SS
2 | Hasdeo Bango (Hy) | 2 | 40 | CSPGCL | SS
3 | Hasdeo Bango (Hy) | 3 | 40 | CSPGCL | SS
4 | Korba (E) extn | 1 | 250 | CSPGCL | SS
5 | Korba (E) extn | 2 | 250 | CSPGCL | SS
6 | Korba (W) | 1 | 210 | CSPGCL | SS
7 | Korba (W) | 2 | 210 | CSPGCL | SS
8 | Korba (W) | 3 | 210 | CSPGCL | SS
9 | Korba (W) | 4 | 210 | CSPGCL | SS |  | 200
10 | Korba (W) | 5 | 500 | CSPGCL | SS
11 | Marwa | 1 | 500 | CSPGCL | SS
|  | Sub total | 2460

## RGMO FGMO_CS
Central Sector
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Gandhar* | 1 | 144.3 | NTPC Ltd | CS
2 | Gandhar* | 2 | 144.3 | NTPC Ltd | CS
3 | Gandhar* | 3 | 144.3 | NTPC Ltd | CS
4 | Gandhar* | 4 | 224.5 | NTPC Ltd | CS
5 | Kawas* | 1 | 106 | NTPC Ltd | CS
6 | Kawas* | 2 | 106 | NTPC Ltd | CS
7 | Kawas* | 3 | 106 | NTPC Ltd | CS
8 | Kawas* | 4 | 106 | NTPC Ltd | CS
9 | Kawas* | 5 | 116 | NTPC Ltd | CS
10 | Kawas* | 6 | 116 | NTPC Ltd | CS
11 | Korba STPS | 1 | 200 | NTPC Ltd | CS
12 | Korba STPS | 2 | 200 | NTPC Ltd | CS
13 | Korba STPS | 3 | 200 | NTPC Ltd | CS
14 | Korba STPS | 4 | 500 | NTPC Ltd | CS
15 | Korba STPS | 5 | 500 | NTPC Ltd | CS
16 | Korba STPS | 6 | 500 | NTPC Ltd | CS
17 | Korba STPS | 7 | 500 | NTPC Ltd | CS
18 | Mouda | 1 | 500 | NTPC Ltd | CS
19 | Mouda | 2 | 500 | NTPC Ltd | CS
20 | Mouda | 3 | 660 | NTPC Ltd | CS
21 | Mouda | 4 | 660 | NTPC Ltd | CS
22 | NSPCL | 1 | 250 | NSPCL | CS
23 | NSPCL | 2 | 250 | NSPCL | CS
24 | Ratnagiri Phase I* | 1 | 205 | RGPPL | CS
25 | Ratnagiri Phase I* | 2 | 205 | RGPPL | CS
26 | Ratnagiri Phase I* | 3 | 230 | RGPPL | CS
27 | Ratnagiri Phase II* | 1 | 213 | RGPPL | CS
28 | Ratnagiri Phase II* | 2 | 213 | RGPPL | CS
29 | Ratnagiri Phase II* | 3 | 237.54 | RGPPL | CS
30 | Ratnagiri Phase III* | 1 | 213 | RGPPL | CS
31 | Ratnagiri Phase III* | 2 | 213 | RGPPL | CS
32 | Ratnagiri Phase III* | 3 | 237.55 | RGPPL | CS
33 | Sipat-I | 2 | 660 | NTPC Ltd | CS
34 | Sipat-I | 3 | 660 | NTPC Ltd | CS
35 | Sipat-II | 4 | 500 | NTPC Ltd | CS
36 | Sipat-II | 5 | 500 | NTPC Ltd | CS
37 | Solapur | 1 | 660 | NTPC Ltd | CS
38 | SSP CBPH (Hy) | 1 | 50 | NCA | CS
39 | SSP CBPH (Hy) | 2 | 50 | NCA | CS
40 | SSP CBPH (Hy) | 3 | 50 | NCA | CS
41 | SSP CBPH (Hy) | 4 | 50 | NCA | CS
42 | SSP CBPH (Hy) | 5 | 50 | NCA | CS
43 | SSP RBPH (Hy) | 1 | 200 | NCA | CS
44 | SSP RBPH (Hy) | 2 | 200 | NCA | CS
45 | SSP RBPH (Hy) | 3 | 200 | NCA | CS
46 | SSP RBPH (Hy) | 4 | 200 | NCA | CS
47 | SSP RBPH (Hy) | 5 | 200 | NCA | CS
48 | SSP RBPH (Hy) | 6 | 200 | NCA | CS
49 | Vindhyachal-I | 1 | 210 | NTPC Ltd | CS
50 | Vindhyachal-I | 2 | 210 | NTPC Ltd | CS
51 | Vindhyachal-I | 3 | 210 | NTPC Ltd | CS
52 | Vindhyachal-I | 4 | 210 | NTPC Ltd | CS
53 | Vindhyachal-I | 5 | 210 | NTPC Ltd | CS
54 | Vindhyachal-I | 6 | 210 | NTPC Ltd | CS
55 | Vindhyachal-II | 7 | 500 | NTPC Ltd | CS
56 | Vindhyachal-II | 8 | 500 | NTPC Ltd | CS
57 | Vindhyachal-III | 9 | 500 | NTPC Ltd | CS
58 | Vindhyachal-III | 10 | 500 | NTPC Ltd | CS
59 | Vindhyachal-IV | 11 | 500 | NTPC Ltd | CS
60 | Vindhyachal-IV | 12 | 500 | NTPC Ltd | CS
61 | Vindhyachal-V | 13 | 500 | NTPC Ltd | CS
|  | Total | 17890.09
* - Effective from 01.10.2017
Private Sector
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Balco | 1 | 300 | Balco | Private
2 | Balco | 2 | 300 | Balco | Private
3 | Balco | 3 | 300 | Balco | Private
4 | Balco | 4 | 300 | Balco | Private
5 | CGPL | 10 | 830 | Tata Power | Private
6 | CGPL | 20 | 830 | Tata Power | Private
7 | CGPL | 30 | 830 | Tata Power | Private
8 | CGPL | 40 | 830 | Tata Power | Private
9 | CGPL | 50 | 830 | Tata Power | Private
10 | DB Power | 1 | 600 | DB Power Ltd. | Private
11 | DB Power | 2 | 600 | DB Power Ltd. | Private
12 | Dhariwal | 2 | 300 | Dhariwal-Infra | Private
13 | GMR Warora (GWEL) | 1 | 300 | GMR Warora (GWEL) | Private
14 | GMR Warora (GWEL) | 2 | 300 | GMR Warora (GWEL) | Private
15 | Essar Power(Mahan) | 1 | 600 | Essar Power(Mahan) | Private
16 | GMR-CG | 1 | 685 | GMR | Private
17 | GMR-CG | 2 | 685 | GMR | Private
18 | Jhabua | 1 | 600 | Jhabua Power Ltd | Private
19 | Jindal Stage-I | 1 | 250 | Jindal Power | Private
20 | Jindal Stage-I | 2 | 250 | Jindal Power | Private
21 | Jindal Stage-I | 3 | 250 | Jindal Power | Private
22 | Jindal Stage-I | 4 | 250 | Jindal Power | Private
23 | Jindal Stage-II | 1 | 600 | Jindal Power | Private
24 | Jindal Stage-II | 2 | 600 | Jindal Power | Private
25 | Jindal Stage-II | 3 | 600 | Jindal Power | Private
26 | Jindal Stage-II | 4 | 600 | Jindal Power | Private
27 | JP-Nigrie | 1 | 660 | Jaypee | Private
28 | JP-Nigrie | 2 | 660 | Jaypee | Private
29 | KSK Mahanadi | 1 | 600 | KSK Mahanadi | Private
30 | KSK Mahanadi | 2 | 600 | KSK Mahanadi | Private
31 | KWPCL | 1 | 600 | KWPCL | Private
32 | Lanco | 1 | 300 | Lanco Amarkantak | Private
33 | Lanco | 2 | 300 | Lanco Amarkantak | Private
34 | MB-Power | 1 | 600 | Hindustan Power Ltd | Private
35 | MB-Power | 2 | 600 | Hindustan Power Ltd | Private
36 | MCCPL | 1 | 300 | ACBIL | Private
37 | RKM | 1 | 360 | RKM | Private
38 | RKM | 2 | 360 | RKM | Private
39 | Sasan_UMPP | 1 | 660 | Reliance Energy | Private
40 | Sasan_UMPP | 2 | 660 | Reliance Energy | Private
41 | Sasan_UMPP | 3 | 660 | Reliance Energy | Private
42 | Sasan_UMPP | 4 | 660 | Reliance Energy | Private
43 | Sasan_UMPP | 5 | 660 | Reliance Energy | Private
44 | Sasan_UMPP | 6 | 660 | Reliance Energy | Private
45 | TRN | 1 | 300 | TRN | Private
46 | TRN | 2 | 300 | TRN | Private
|  | Total | 23920

## IR
Path Details | Voltage(kV) | Link Details | Owner | No. of Circuits | Length(in circuit km) |  | 765 | 400 | HVDC
WR-NR | 400 | HVDC Vindhyachal Back to Back (500 MW) | NRTS-1 | 2 blocks | - | ER | 4 | 6
| +/-500 | HVDC APL(Mundra)-Mohindargarh (2500MW)-Bipole | ATIL | Bipole | 1978 | SR | 2 | 2 | 2
| 800 | HVDC Champa-Kurukshetra (3000MW) Bipole | NRTS-1/WRTS-1 | Bipole | 1306
| 765 | Gwalior-Agra | NRTS-1/WRTS-2 | D/C | 258 | NR | 4 | 5 | 4
|  | Gwalior-Jaipur | NRTS-1/WRTS-2 | D/C | 615
| 400 | Zerda-Kankroli | WRTS-2/NRTS-1 | S/C | 234
|  | Zerda-Bhinmal | WRTS-2/NRTS-1 | S/C | 143
|  | Shujalpur-RAPP | RTCL | D/C | 402
|  | Vindhyachal PS-Rihand | WRTS-2/NRTS-1 | D/C | 60
| 220 | Badod-Sakatpur | Madhya Pradesh / Rajasthan | S/C | 199
|  | Bhanpura-Modak | Madhya Pradesh / Rajasthan | S/C | 45
|  | Mehgaon-Auraiya | Madhya Pradesh / Uttar Pradesh | S/C | 113
|  | Malanpur-Auraiya | Madhya Pradesh / Uttar Pradesh | S/C | 146
| 132 | Neemuch-Nimbahera | Madhya Pradesh / Rajasthan | S/C | 45
|  | Seopur Kalan-Sawai Madhopur (Khandar) | Madhya Pradesh / Rajasthan | S/C | 62
|  | Gandhi Sagar-Ranapratap Sagar-I&II | Madhya Pradesh / Rajasthan | D/C | 102
|  | Bina-Morwa | Madhya Pradesh / Uttar Pradesh | S/C | 9
|  | Rajghat-Lalitpur | Madhya Pradesh / Uttar Pradesh | S/C | 23
WR-SR | 765 | Sholapur-Raichur | WRTS-1 | D/C | 416
|  | Wardha-Nizamabad | WRTS-1/SRTS-1 | D/C | 391
| 400 | Bhadravati Back to Back (2x500 MW) | WRTS-1 | 2 blocks | -
|  | Bhadravati HVDC-Ramagundam | WRTS-1/SRTS-1 | D/C | 356
|  | Kholpaur-PG-Kudgi | WRTS-1/SRTS-1 | D/C | 392
| 220 | Kolhaphur(Mudshingi)-Chikkodi | MSETCL,KPTCL | S/C | 155
| 220 | Kolhaphur(Talandage)-Chikkodi | MSETCL,KPTCL | S/C | 150
|  | Ponda-Ambewadi | GED, KPTCL | S/C | 42
|  | Xeldem-Ambewadi | GED, KPTCL | S/C | 48
WR-ER | 400 | Raigarh-Jharsuguda | WRTS-1 | D/C | 142
|  | Raigarh-Sterlite | WRTS-1 | S/C | 99
|  | Raigarh-Rourkella | WRTS-1 | S/C | 209
|  | Sipat-Ranchi | WRTS-1 | D/C | 810
| 765 | Dharamjaigarh-Ranchi | WRTS-1 | D/C | 303
|  | Dharamjaigarh-Jharsuguda | WRTS-1 | D/C | 606
| 220KV | Raigarh-Budhipadar | OPTCL/CSPTCL | S/C | 105
|  | Korba(East)-II-Budhipadar | OPTCL/CSPTCL | D/C | 176
D/C : Double Circuit, S/C: Single Circuit

## RGMO FGMO
NTPC
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Korba STPS | 1 | 200 | NTPC Ltd | CS
2 | Korba STPS | 2 | 200 | NTPC Ltd | CS
3 | Korba STPS | 3 | 200 | NTPC Ltd | CS
4 | Korba STPS | 4 | 500 | NTPC Ltd | CS
5 | Korba STPS | 5 | 500 | NTPC Ltd | CS
6 | Korba STPS | 6 | 500 | NTPC Ltd | CS
7 | Korba STPS | 7 | 500 | NTPC Ltd | CS
8 | Mouda | 1 | 500 | NTPC Ltd | CS
9 | Mouda | 2 | 500 | NTPC Ltd | CS
10 | Mouda | 3 | 660 | NTPC Ltd | CS
11 | Mouda | 4 | 660 | NTPC Ltd | CS
12 | Sipat-I | 1 | 660 | NTPC Ltd | CS
13 | Sipat-I | 2 | 660 | NTPC Ltd | CS
14 | Sipat-I | 3 | 660 | NTPC Ltd | CS
15 | Sipat-II | 4 | 500 | NTPC Ltd | CS
16 | Sipat-II | 5 | 500 | NTPC Ltd | CS
17 | Vindhyachal-I | 1 | 210 | NTPC Ltd | CS
18 | Vindhyachal-I | 2 | 210 | NTPC Ltd | CS
19 | Vindhyachal-I | 3 | 210 | NTPC Ltd | CS
20 | Vindhyachal-I | 4 | 210 | NTPC Ltd | CS
21 | Vindhyachal-I | 5 | 210 | NTPC Ltd | CS
22 | Vindhyachal-I | 6 | 210 | NTPC Ltd | CS
23 | Vindhyachal-II | 7 | 500 | NTPC Ltd | CS
24 | Vindhyachal-II | 8 | 500 | NTPC Ltd | CS
25 | Vindhyachal-III | 9 | 500 | NTPC Ltd | CS
26 | Vindhyachal-III | 10 | 500 | NTPC Ltd | CS
27 | Vindhyachal-IV | 11 | 500 | NTPC Ltd | CS
28 | Vindhyachal-IV | 12 | 500 | NTPC Ltd | CS
29 | Vindhyachal-V | 13 | 500 | NTPC Ltd | CS
|  | Sub Total | 12660
NCA
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | SSP CBPH (Hy) | 1 | 50 | NCA | CS
2 | SSP CBPH (Hy) | 2 | 50 | NCA | CS
3 | SSP CBPH (Hy) | 3 | 50 | NCA | CS
4 | SSP CBPH (Hy) | 4 | 50 | NCA | CS
5 | SSP CBPH (Hy) | 5 | 50 | NCA | CS
6 | SSP RBPH (Hy) | 1 | 200 | NCA | CS
7 | SSP RBPH (Hy) | 2 | 200 | NCA | CS
8 | SSP RBPH (Hy) | 3 | 200 | NCA | CS
9 | SSP RBPH (Hy) | 4 | 200 | NCA | CS
10 | SSP RBPH (Hy) | 5 | 200 | NCA | CS
11 | SSP RBPH (Hy) | 6 | 200 | NCA | CS
|  | Sub Total | 1450
CGPL
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | CGPL | 10 | 830 | Tata Power | Private
2 | CGPL | 20 | 830 | Tata Power | Private
3 | CGPL | 30 | 830 | Tata Power | Private
4 | CGPL | 40 | 830 | Tata Power | Private
5 | CGPL | 50 | 830 | Tata Power | Private
|  | Sub Total | 4150
Sasan
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Sasan_UMPP | 1 | 660 | Reliance Energy | Private
2 | Sasan_UMPP | 2 | 660 | Reliance Energy | Private
3 | Sasan_UMPP | 3 | 660 | Reliance Energy | Private
4 | Sasan_UMPP | 4 | 660 | Reliance Energy | Private
5 | Sasan_UMPP | 5 | 660 | Reliance Energy | Private
6 | Sasan_UMPP | 6 | 660 | Reliance Energy | Private
|  | Sub Total | 3960
Essar (Mahan)
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Essar Power(Mahan) | 1 | 600 | Essar Power(Mahan) | Private
KSK
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | KSK Mahanadi | 1 | 600 | KSK Mahanadi | Private
2 | KSK Mahanadi | 2 | 600 | KSK Mahanadi | Private
|  | Sub Total | 1200
DB-Power
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | DB Power | 1 | 600 | DB Power Ltd. | Private
2 | DB Power | 2 | 600 | DB Power Ltd. | Private
LANCO
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Lanco | 1 | 300 | Lanco Amarkantak | Private
2 | Lanco | 2 | 300 | Lanco Amarkantak | Private
|  | Sub Total | 600
JPL
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Jindal TPP | 1 | 250 | Jindal Power | Private
2 | Jindal TPP | 2 | 250 | Jindal Power | Private
3 | Jindal TPP | 3 | 250 | Jindal Power | Private
4 | Jindal TPP | 4 | 250 | Jindal Power | Private
5 | JPL IPP | 1 | 600 | Jindal Power | Private
6 | JPL IPP | 2 | 600 | Jindal Power | Private
7 | JPL IPP | 3 | 600 | Jindal Power | Private
|  | Sub Total | 2800
JP-Nigrie
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | JP-Nigrie | 1 | 660 | Jaypee | Private
2 | JP-Nigrie | 2 | 660 | Jaypee | Private
1320
MB Power
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | MB-Power | 1 | 600 | Hindustan Power Ltd | Private
2 | MB-Power | 2 | 600 | Hindustan Power Ltd | Private
KWPCL
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | KWPCL | 1 | 600 | KWPCL | Private
Dhariwal
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | Dhariwal | 2 | 300 | Dhariwal-Infra | Private
GMR-CG
Sl. No | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Utility | Sector (CS/SS/Private)
1 | GMR-CG | 1 | 685 | GMR | Private
2 | GMR-CG | 2 | 685 | GMR | Private
EMCO
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | EMCO | 1 | 300 | EMCO | Private
2 | EMCO | 2 | 300 | EMCO | Private
|  | Sub-Total | 600
Balco
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | Balco | 1 | 300 | Balco | Private
2 | Balco | 2 | 300 | Balco | Private
3 | Balco | 4 | 300 | Balco | Private
|  | Sub-Total | 900
RKM
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | RKM | 1 | 360 | RKM | Private
2 | RKM | 2 | 360 | RKM | Private
|  | Sub-Total | 720
MCCPL
Sl. No. | Name of Station | Name of Stage/ Unit | Installed capacity (MW) | Name of Uitlity | Sector (CS/SS/Private)
1 | MCCPL | 1 | 300 | ACBIL | Private

## 400 SC MVA
Sl. No | BUS | kV | Three Phase Fault
|  |  | Three phase fault current (kA) | Three phase fault MVA
1 | ACBIL | 400 | 15.6374 | 10833.5907
2 | Akola-II | 400 | 24.4818 | 16960.991
3 | Akola-II | 400 | 22.7922 | 15790.4362
4 | Alkud(MSETCL | 400 | 9.2837 | 6431.7474
5 | Amreli | 400 | 13.2652 | 9190.1306
6 | APL Mundra | 400 | 36.0476 | 24973.7773
7 | APML Tirora | 400 | 21.9344 | 15196.1523
8 | ASHTA | 400 | 8.4297 | 5840.0962
9 | Asoj | 400 | 38.1019 | 26396.9963
10 | Athena | 400 | 30.6573 | 21239.3774
11 | Aurangabad | 400 | 29.9473 | 20747.4894
12 | Aurangabad-PG | 400 | 35.3376 | 24481.8893
13 | Bableshwar | 400 | 27.038 | 18731.9264
14 | Balco-CTU | 400 | 21.3269 | 14775.2763
15 | Betul GIS | 400 | 15.0714 | 10441.4659
16 | Bhachau | 400 | 33.6851 | 23337.0373
17 | Bhatapara-PG | 400 | 13.8255 | 9578.3064
18 | Bhhadrawati | 400 | 44.5483 | 30863.0622
19 | Bhilai | 400 | 39.1882 | 27149.585
20 | Bhopal-BDTCL | 400 | 32.8569 | 22763.2603
21 | Bhopal-MP | 400 | 34.8974 | 24176.9187
22 | Bhusawal | 400 | 19.6047 | 13582.1362
23 | Bilaspur-PS | 400 | 33.9213 | 23500.6766
24 | Bina-MP | 400 | 39.2992 | 27226.4858
25 | Bina-PG | 400 | 39.4303 | 27317.3118
26 | Bina-Satna 3 | 400 | 3.8854 | 2691.8051
27 | Bina-Satna G | 400 | 3.8986 | 2700.9501
28 | Birsingpur | 400 | 18.6963 | 12952.7966
29 | Boisar | 400 | 28.5612 | 19787.1994
30 | CGPL | 400 | 29.275 | 20281.72
31 | Chakan | 400 | 20.374 | 14115.1072
32 | Champa-PS | 400 | 45.8112 | 31737.9994
33 | Chandrapur | 400 | 53.189 | 36849.3392
34 | Chandrpr-II | 400 | 52.5887 | 36433.4514
35 | Chandrpur GCR | 400 | 49.7646 | 34476.9149
36 | Charanka | 400 | 2.2134 | 1533.4435
37 | Chegaon | 400 | 10.6349 | 7367.8587
38 | Chornia | 400 | 31.2944 | 21680.7603
39 | Damoh-PG | 400 | 13.8283 | 9580.2462
40 | DB Power | 400 | 35.81 | 24809.168
41 | Deepnagar | 400 | 19.1523 | 13268.7134
42 | Dehgam | 400 | 35.1621 | 24360.3029
43 | Dgen | 400 | 9.068 | 6282.3104
44 | Dharamjaygarh | 400 | 28.0529 | 19435.0491
45 | Dhariwal | 400 | 40.3405 | 27947.8984
46 | Dhariwal-CTU | 400 | 24.8825 | 17238.596
47 | Dhule | 400 | 26.1122 | 18090.5322
48 | Dhule-BDTCL | 400 | 24.7096 | 17118.8109
49 | Ektuni | 400 | 22.0299 | 15262.3147
50 | EMCO | 400 | 25.4861 | 17656.7701
51 | Gandhar-NTPC | 400 | 28.1142 | 19477.5178
52 | GMR-GCEL | 400 | 15.8978 | 11013.9958
53 | GPEC | 400 | 22.3324 | 15471.8867
54 | Gwalior-PG | 400 | 24.3792 | 16889.9098
55 | Hadala | 400 | 17.602 | 12194.6656
56 | Hazira | 400 | 9.4564 | 6551.3939
57 | IEPL | 400 | 11.2264 | 7777.6499
58 | Indirasagar | 400 | 19.4224 | 13455.8387
59 | Indore-MP | 400 | 34.0479 | 23588.3851
60 | Indore-PG | 400 | 34.3259 | 23780.9835
61 | Itarsi-PG | 400 | 35.8135 | 24811.5928
62 | Jabalpur-PG | 400 | 35.8534 | 24839.2355
63 | Jabalpur-PS | 400 | 37.6869 | 26109.4843
64 | Jagdalpur | 400 | 1.9555 | 1354.7704
65 | Jaigad | 400 | 19.8623 | 13760.6014
66 | Jaypee Nigrie | 400 | 14.6439 | 10145.2939
67 | Jejuri | 400 | 14.1949 | 9834.2267
68 | Jetpur | 400 | 13.3573 | 9253.9374
69 | Jhabua | 400 | 13.8899 | 9622.9227
70 | JP Bina | 400 | 27.6417 | 19150.1698
71 | JPL Stage-I | 400 | 33.6279 | 23297.4091
72 | JPL Stage-II | 400 | 35.5532 | 24631.257
73 | Julwnia | 400 | 7.6873 | 5325.7614
74 | Kakrapar-34 | 400 | 16.6335 | 11523.6888
75 | Kala-PG | 400 | 19.2384 | 13328.3635
76 | Kalwa | 400 | 23.3022 | 16143.7642
77 | Karad | 400 | 21.8122 | 15111.4922
78 | Kasor | 400 | 21.7361 | 15058.7701
79 | Katni | 400 | 11.7805 | 8161.5304
80 | KHAC2 | 400 | 5.2716 | 3652.1645
81 | KHACS1 | 400 | 5.2716 | 3652.1645
82 | Khandwa-PG | 400 | 30.807 | 21343.0896
83 | Kharghar | 400 | 18.1358 | 12564.4822
84 | Kolhapur-MS | 400 | 18.3009 | 12678.8635
85 | Kolhapur-PG | 400 | 14.9122 | 10331.1722
86 | Koradi | 400 | 22.3932 | 15514.009
87 | Koradi-II | 400 | 22.1338 | 15334.2966
88 | Koradi-III | 400 | 22.2479 | 15413.3451
89 | Korba-NTPC | 400 | 51.0058 | 35336.8182
90 | Korba-WEST | 400 | 37.8485 | 26221.4408
91 | Korba-W-EXTN | 400 | 36.808 | 25500.5824
92 | Kosamba | 400 | 24.529 | 16993.6912
93 | Koyna | 400 | 21.7534 | 15070.7555
94 | KSK Mahanadi | 400 | 29.4105 | 20375.5944
95 | KWPCL | 400 | 31.0796 | 21531.9469
96 | Lancopathadi | 400 | 23.0728 | 15984.8358
97 | Lara-NTPC | 400 | 35.5489 | 24628.2779
98 | Lonikhand | 400 | 24.4013 | 16905.2206
99 | LonikhandII | 400 | 24.1421 | 16725.6469
100 | Magarwada | 400 | 16.0755 | 11137.1064
101 | Mahan | 400 | 18.1816 | 12596.2125
102 | Mansr-Halvad | 400 | 12.3845 | 8579.9816
103 | Mapusa | 400 | 6.1303 | 4247.0718
104 | Marwa | 400 | 22.1482 | 15344.273
105 | Mauda-NTPC | 400 | 21.8088 | 15109.1366
106 | MB Power | 400 | 14.3591 | 9947.9845
107 | MCCPL | 400 | 15.7094 | 10883.4723
108 | Nagda | 400 | 25.3108 | 17535.3222
109 | Nagothane | 400 | 16.0413 | 11113.4126
110 | Nandangaonpeth | 400 | 14.8316 | 10275.3325
111 | Nanded | 400 | 12.5569 | 8699.4203
112 | Nasik-Sinner | 400 | 13.1246 | 9092.7229
113 | Navsari-PG | 400 | 21.0865 | 14608.7272
114 | New Khapkhada | 400 | 22.0526 | 15278.0413
115 | New-Koyna | 400 | 24.1081 | 16702.0917
116 | NHPTL-Bina | 400 | 38.553 | 26709.5184
117 | NICOL-Torren | 400 | 20.3932 | 14128.409
118 | NSPCL | 400 | 31.649 | 21926.4272
119 | Padghe | 400 | 28.8043 | 19955.619
120 | Parli-MS | 400 | 27.4313 | 19004.4046
121 | Parli-PG | 400 | 27.8364 | 19285.0579
122 | Pirana_P | 400 | 25.4545 | 17634.8776
123 | Pirana_T | 400 | 23.7375 | 16445.34
124 | Pithampur | 400 | 19.5546 | 13547.4269
125 | Pune GIS-PG | 400 | 25.3072 | 17532.8282
126 | Pune-PG | 400 | 26.7277 | 18516.9506
127 | Raigarh-PG | 400 | 49.7557 | 34470.749
128 | Raigarh-PS | 400 | 52.1188 | 36107.9046
129 | Raipur-PG | 400 | 38.5389 | 26699.7499
130 | Raipur-PG-II | 400 | 36.8943 | 25560.371
131 | Raipur-PS | 400 | 36.3525 | 25185.012
132 | Raipur-TCSC1 | 400 | 36.8943 | 25560.371
133 | Raipur-TCSC2 | 400 | 36.8943 | 25560.371
134 | Raipur-TCSC3 | 400 | 38.5389 | 26699.7499
135 | Raipur-TCSC4 | 400 | 38.5389 | 26699.7499
136 | Raita | 400 | 26.3512 | 18256.1114
137 | Rajgarh | 400 | 22.6147 | 15667.4642
138 | Rajg-FS1 | 400 | 22.6147 | 15667.4642
139 | Rajg-FS2 | 400 | 22.6147 | 15667.4642
140 | Ranchodpura | 400 | 29.0217 | 20106.2338
141 | RGPPL | 400 | 18.8981 | 13092.6037
142 | RKM | 400 | 31.6372 | 21918.2522
143 | Sami | 400 | 13.1415 | 9104.4312
144 | Sami_FSC | 400 | 13.6258 | 9439.9542
145 | Sami-F2 | 400 | 13.6258 | 9439.9542
146 | Sasanbypass | 400 | 19.7448 | 13679.1974
147 | Sasan-UMPP | 400 | 35.1866 | 24377.2765
148 | Satna-PG | 400 | 36.3374 | 25174.5507
149 | Satpura | 400 | 24.5313 | 16995.2846
150 | Seoni-PG | 400 | 34.1652 | 23669.6506
151 | Siipatbypass | 400 | 34.7917 | 24103.6898
152 | Singaji | 400 | 15.6431 | 10837.5397
153 | Sipat-NTPC | 400 | 34.7917 | 24103.6898
154 | SKS | 400 | 28.9622 | 20065.0122
155 | Soja | 400 | 21.7187 | 15046.7154
156 | Solapur-MS | 400 | 10.4603 | 7246.8958
157 | Solapur-NTPC | 400 | 27.2829 | 18901.5931
158 | Solapur-PG | 400 | 29.5227 | 20453.3266
159 | SSP | 400 | 24.2547 | 16803.6562
160 | SSP_II | 400 | 24.2547 | 16803.6562
161 | Sugen | 400 | 24.7277 | 17131.3506
162 | Sujalpur-PG | 400 | 17.8134 | 12341.1235
163 | Tamnar-PS | 400 | 36.5237 | 25303.6194
164 | Taptithanda | 400 | 21.6044 | 14967.5283
165 | Tarapur-3&4 | 400 | 26.2307 | 18172.629
166 | TRN Energy | 400 | 26.7463 | 18529.8366
167 | Ukai | 400 | 18.4386 | 12774.2621
168 | Uno-Sugen | 400 | 22.7462 | 15758.5674
169 | Vadinar | 400 | 9.8681 | 6836.6197
170 | Vadodara-PS | 400 | 35.3879 | 24516.7371
171 | Vapi | 400 | 20.9991 | 14548.1765
172 | Veloda Sankr | 400 | 3.0012 | 2079.2314
173 | Versana | 400 | 33.3375 | 23096.22
174 | Vindh-IV | 400 | 27.1875 | 18835.5
175 | Vindhyachal-PS | 400 | 38.6898 | 26804.2934
176 | Vindycl-NTPC | 400 | 39.4015 | 27297.3592
177 | Wanakbori | 400 | 19.5972 | 13576.9402
178 | Wardha_FSC1 | 400 | 6.9646 | 4825.0749
179 | Wardha_FSC2 | 400 | 6.9646 | 4825.0749
180 | Warora | 400 | 40.6916 | 28191.1405
181 | Zerda | 400 | 19.3551 | 13409.2133
182 | Vindhyachal-V | 400 | 35.8407 | 24830.437
183 | Wardha-PG | 400 | 56.6 | 39212.48

## 500MVA ICTs
Sl. No | Sub-station | Id | MVA | Voltage Ratio | Owner
1 | Alkud | 1 | 500 | 400/220 | MSETCL
2 | Asoj | 1 | 500 | 400/220 | GETCO | G
3 | Asoj | 2 | 500 | 400/220 | GETCO | G
4 | Aurangabad | 3 | 500 | 400/220 | MSETCL
5 | Bableshwar | 3 | 500 | 400/220 | MSETCL
6 | Birsingpur | 1 | 500 | 400/220 | MPPTCL
7 | Boisar | 3 | 500 | 400/220 | WRTS-1
8 | Chorania | 1 | 500 | 400/220 | GETCO | G
9 | Chorania | 2 | 500 | 400/220 | GETCO | G
10 | Damoh | 3 | 500 | 400/220 | WRTS-2
11 | Deepnagar | 1 | 500 | 400/220 | MSETCL
12 | Deepnagar | 2 | 500 | 400/220 | MSETCL
13 | Dhule | 3 | 500 | 400/220 | MSETCL
14 | Gandhar | 1 | 500 | 400/220 | NTPC | G
15 | Gandhar | 2 | 500 | 400/220 | NTPC | G
16 | Gpec | 1 | 500 | 400/220 | GETCO | G
17 | Hazira | 1 | 500 | 400/220 | ESSAR | G
18 | Hazira | 2 | 500 | 400/220 | ESSAR | G
19 | Hazira | 3 | 500 | 400/220 | ESSAR | G
20 | Jejuri | 1 | 500 | 400/220 | MSETCL
21 | Jejuri | 2 | 500 | 400/220 | MSETCL
22 | Jetpur | 4 | 500 | 400/220 | GETCO | G
23 | Kalwa | 1 | 500 | 400/220 | MSETCL
24 | Kalwa | 2 | 600 | 400/220 | MSETCL
25 | Kalwa | 3 | 500 | 400/220 | MSETCL
26 | Khaparkheda | 1 | 500 | 400/220 | MSETCL
27 | Khaparkheda | 2 | 500 | 400/220 | MSETCL
28 | Kolhapur | 3 | 500 | 400/220 | MSETCL
29 | Koradi-II | 1 | 500 | 400/220
30 | Korba (W) | 1 | 500 | 400/220 | CSEPTCL
31 | Lonikhand-2 | 1 | 500 | 400/220 | MSETCL
32 | Lonikhand-2 | 2 | 500 | 400/220 | MSETCL
33 | Nagothane | 3 | 500 | 400/220 | MSETCL
34 | Navasari | 3 | 500 | 400/220 | WRTS-2 | G
35 | New Koyna | 2 | 500 | 400/220 | MSETCL
36 | Padghe | 4 | 600 | 400/220 | MSETCL
37 | Parli | 3 | 500 | 400/220 | MSETCL
38 | Satpura | 1 | 500 | 400/220 | MPPTCL
39 | Sholapur | 1 | 500 | 400/220 | MSETCL
40 | Sholapur | 2 | 500 | 400/220 | MSETCL
41 | Solapur | 3 | 500 | 400/220 | PGCIL
42 | Soja | 1 | 500 | 400/220 | GETCO | G
43 | Soja | 2 | 500 | 400/220 | GETCO | G
44 | Taptithanda | 1 | 500 | 400/220 | MSETCL
45 | Vadodara-PS | 1 | 500 | 400/220 | WRTS-II
46 | Vadodara-PS | 2 | 500 | 400/220 | WRTS-II
47 | Warora | 1 | 500 | 400/220 | MEGPTL
48 | Warora | 2 | 500 | 400/220 | MEGPTL
|  | Sub-Total | 23700

## New Elements
Element name
Khandwa-Indore D/C
Khandwa-Betul D/C
Mouda-Betul D/C
Damoh ICT-3
APCL-Kotra
KWPCL-Kotra
Balco-Dharamjaygarh
KSK-Champa
RKM-Kotra
TRN
Champa ICTs
Koradi II ICT
Warora ICT Shifting
Champa Filters
Switchable Reactors NGR
Asoj ICT-4
Korba-Birsingpur
220 kV Bhugoan-Pusad lilo at Deoli
SSP-Rajgarh LRs at rajgarh
765 kV Champa-Durg-2
765 kV Champa-Dharamjaygarh
Betul ICTs -1 & 2
Betul BR 125
Bableshwar ICT-4
Orientation of Phadge-Kharghar and Padghe-Pune as Kharghar-Pune

## 1500MVA ICTs
Sl. No | Sub-Station | Id | MVA | Voltage Ratio | Owner
1 | Akola(2) | 1 | 1500 | 765/400 | MEGPTCL
2 | Aurangabad | 1 | 1500 | 765/400 | WRTS-1
3 | Aurangabad | 2 | 1500 | 765/400 | WRTS-1
4 | Bhopal-BDTCL | 1 | 1500 | 765/400 | BDTCL
5 | Bhopal-BDTCL | 2 | 1500 | 765/400 | BDTCL
6 | Bilaspur | 1 | 1500 | 765/400 | WRTS-1
7 | Bilaspur | 2 | 1500 | 765/400 | WRTS-1
8 | Bilaspur | 3 | 1500 | 765/400 | WRTS-1
9 | Champa | 1 | 1500 | 765/400 | WRTS-1
10 | Champa | 2 | 1500 | 765/400 | WRTS-1
11 | Champa | 3 | 1500 | 765/400 | WRTS-1
12 | Champa | 4 | 1500 | 765/400 | WRTS-1
13 | Champa | 5 | 1500 | 765/400 | WRTS-1
14 | Champa | 6 | 1500 | 765/400 | WRTS-1
15 | Dhule-BDTCL | 2 | 1500 | 765/400 | BDTCL
16 | Gwalior | 1 | 1500 | 765/400 | WRTS-2
17 | Gwalior | 2 | 1500 | 765/400 | WRTS-2
18 | Indore | 1 | 1500 | 765/400 | WRTS-2
19 | Indore | 2 | 1500 | 765/400 | WRTS-2
20 | Jabalpur-PS | 1 | 1500 | 765/400 | WRTS-2
21 | Jabalpur-PS | 2 | 1500 | 765/400 | WRTS-2
22 | Koradi-III | 1 | 1500 | 765/400 | MEGPTCL
23 | Koradi-III | 2 | 1500 | 765/400 | MEGPTCL
24 | Pune (Shikrapur) | 1 | 1500 | 765/400 | WRTS-1
25 | Pune (Shikrapur) | 2 | 1500 | 765/400 | WRTS-1
26 | Raigarh-PS(kotra) | 1 | 1500 | 765/400 | WRTS-1
27 | Raigarh-PS(kotra) | 2 | 1500 | 765/400 | WRTS-1
28 | Raigarh-PS(kotra) | 3 | 1500 | 765/400 | WRTS-1
29 | Raigarh-PS(kotra) | 4 | 1500 | 765/400 | WRTS-1
30 | Raipur-PS(Durg) | 1 | 1500 | 765/400 | WRTS-1
31 | Raipur-PS(Durg) | 2 | 1500 | 765/400 | WRTS-1
32 | Seoni | 1 | 1500 | 765/400 | WRTS-1
33 | Seoni | 2 | 1500 | 765/400 | WRTS-1
34 | Seoni | 3 | 1500 | 765/400 | WRTS-1
35 | Sholapur-PG | 1 | 1500 | 765/400 | WRTS-1
36 | Sholapur-PG | 2 | 1500 | 765/400 | WRTS-1
37 | Tamnar-PS | 1 | 1500 | 765/400 | WRTS-1
38 | Tamnar-PS | 2 | 1500 | 765/400 | WRTS-1
39 | Tamnar-PS | 3 | 1500 | 765/400 | WRTS-1
40 | Tamnar-PS | 4 | 1500 | 765/400 | WRTS-1
41 | Tiroda | 1 | 1500 | 765/400 | APML
42 | Vadodara-PS | 1 | 1500 | 765/400 | WRTS-2
43 | Vadodara-PS | 2 | 1500 | 765/400 | WRTS-2
44 | Vindhyachal-PS | 1 | 1500 | 765/400 | WRTS-2
45 | Vindhyachal-PS | 2 | 1500 | 765/400 | WRTS-2
46 | Wardha | 1 | 1500 | 765/400 | WRTS-1
47 | Wardha | 2 | 1500 | 765/400 | WRTS-1
48 | Wardha | 3 | 1500 | 765/400 | WRTS-1
|  | Sub-Total | 72000

## 1000MVA ICTs
Sl No | Sub-station | From Bus Voltage | To Bus Name | To Bus Voltage | Id | MVA | Voltage Ratio | Owner
1 | BINA-PG | 400 | BINA-PG | 765 | 1 | 1000 | 765/400 | WRTS-2
2 | BINA-PG | 400 | BINA-PG | 765 | 2 | 1000 | 765/400 | WRTS-2
3 | Sasan | 400 | SASAN | 765 | 1 | 1000 | 765/400 | Reliance
4 | Sasan | 400 | SASAN | 765 | 2 | 1000 | 765/400 | Reliance
5 | Satna | 400 | SATNA | 765 | 1 | 1000 | 765/400 | WRTS-2
6 | Satna | 400 | SATNA | 765 | 2 | 1000 | 765/400 | WRTS-2
7 | Sipat | 400 | SIPAT | 765 | 1 | 1000 | 765/400 | NTPC
8 | Sipat | 400 | SIPAT | 765 | 2 | 1000 | 765/400 | NTPC
[5 empty] | Sub-total | 8000

## MP
400 kV Lines
Sl No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Length(in Km) | Conductor Type
1 | Bhopal | Bina-MP | 1 | MPPTCL | MPPTCL | MPPTCL | 289 | Twin ACSR Moose
2 | Bhopal | Bina-MP | 2 | MPPTCL | MPPTCL | MPPTCL | 273 | Twin ACSR Moose
3 | Bhopal | Itarsi | 1 | MPPTCL | MPPTCL | WRST-2 | 98 | Twin ACSR Moose
4 | Bhopal | Itarsi | 2 | MPPTCL | MPPTCL | WRST-2 | 98 | Twin ACSR Moose
5 | Bina-MP | JP-Bina | 1 | MPPTCL | MPPTCL | Jaypee | 20 | Twin ACSR Moose
6 | Birsingpur | Katni | 1 | MPPTCL | MPPTCL | MPPTCL | 118 | Twin ACSR Moose
7 | Birsingpur | Katni | 2 | MPPTCL | MPPTCL | MPPTCL | 118 | Twin ACSR Moose
8 | Chhegaon | Julwania | 1 | MPPTCL | MPPTCL | MPPTCL | 114 | Twin ACSR Moose
9 | Damoh | Katni | 1 | MPPTCL | WRTS-2 | MPPTCL | 118 | Twin ACSR Moose
10 | Indira Sagar | Indore-MP | 1 | MPPTCL | MPPTCL | MPPTCL | 79 | Quad ACSR Moose
11 | Indira Sagar | Indore-MP | 2 | MPPTCL | MPPTCL | MPPTCL | 80 | Quad ACSR Moose
12 | Indira Sagar | Nagda | 1 | MPPTCL | MPPTCL | MPPTCL | 188 | Twin ACSR Moose
13 | Indore-MP | Nagda | 1 | MPPTCL | MPPTCL | MPPTCL | 108 | Twin ACSR Moose
14 | Indore-MP | Pithampur | 1 | MPPTCL | MPPTCL | MPPTCL | 150 | Twin ACSR Moose
15 | Indore-MP | Pithampur | 2 | MPPTCL | MPPTCL | MPPTCL | 150 | Twin ACSR Moose
16 | Malwa | Chhegaon | 1 | MPPTCL | MPPTCL | MPPTCL | 53 | Twin ACSR Moose
17 | Malwa | Pithampur | 1 | MPPTCL | MPPTCL | MPPTCL | 136 | Twin ACSR Moose
18 | Malwa | Pithampur | 2 | MPPTCL | MPPTCL | MPPTCL | 136 | Twin ACSR Moose
19 | Nagda | Indira Sagar | 1 | MPPTCL | MPPTCL | MPPTCL | 103 | Twin ACSR Moose
20 | Satpura | Indira-sagar | 1 | MPPTCL | MPPTCL | MPPTCL | 189 | Twin ACSR Moose
21 | Satpura | Astha | 1 | MPPTCL | MPPTCL | MPPTCL | 240 | Twin ACSR Moose
22 | SSP | Rajgarh | 1 | MPPTCL | SSNNL | MPPTCL | 178 | Twin ACSR Moose
23 | SSP | Rajgarh | 2 | MPPTCL | SSNNL | MPPTCL | 178 | Twin ACSR Moose
[6 empty] | Total | 3214
Important 220 kV Lines in MP
S.No | End-1 | End-2 | Id | Line Owner | End-1 Owner | End-2 Owner | Length(in Km) | Conductor Type
1 | Anuppur | Kotmikala | 1 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
2 | Anuppur | Kotmikala | 2 | MPPTCL | CSPTCL | MPPTCL | 61 | Single Zebra
3 | Auraiya | Malanpur | 1 | MPPTCL | UPPTCL | MPPTCL | 146 | Single Zebra
4 | Auraiya | Mehgaon | 1 | MPPTCL | UPPTCL | MPPTCL | 113 | Single Zebra
5 | Badod | Sakatpur | 1 | MPPTCL | MPPTCL | RSPTCL | 199 | Single Zebra
6 | Badod | Modak | 1 | MPPTCL | MPPTCL | RSPTCL | 151 | Single Zebra
7 | Bina-MP | Bina-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
8 | Bina-MP | Shivpuri | 1 | MPPTCL | MPPTCL | MPPTCL | 169 | Single Zebra
9 | Bina-MP | Mahalgaon | 1 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
10 | Bina-MP | Mahalgaon | 2 | MPPTCL | MPPTCL | MPPTCL | 246 | Single Zebra
11 | Damoh-MP | Damoh-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 8 | Single Zebra
12 | Damoh-MP | Damoh-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 9 | Single Zebra
13 | Damoh-PG | Sagar | 2 | MPPTCL | WRTS-2 | MPPTCL | 62 | Single Zebra
14 | Damoh-PG | Tikamgad | 1 | MPPTCL | WRTS-2 | MPPTCL | 151 | Single Zebra
15 | Gwalior | Malanpur | 1 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
16 | Gwalior | Malanpur | 2 | MPPTCL | WRTS-2 | MPPTCL | 38 | Single Zebra
17 | Gwalior | Mahalgaon | 1 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
18 | Gwalior | Mahalgaon | 2 | MPPTCL | WRTS-2 | MPPTCL | 11 | Single Zebra
19 | Hoshangabad | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 21 | Single Zebra
20 | Itarsi | Itarsi-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 3 | Single Zebra
21 | Jabalpur | Jabalpur-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
22 | Jabalpur | Jabalpur-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 11 | Single Zebra
23 | Katni | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 102 | Single Zebra
24 | Khandwa | Omkareswar | 1 | MPPTCL | WRTS-2 | MPPTCL | 98 | Single Zebra
25 | Mehgaon | Malanpur | 1 | MPPTCL | MPPTCL | MPPTCL | 37 | Single Zebra
26 | Pandurna | Kalmeshwar | 1 | MSETCL/MPPTCL | MPPTCL | MSETCL | 68 | Single Zebra
27 | Pithampura | Rajgarh-PG | 1 | MPPTCL | MPPTCL | WRTS-1 | 79 | Single Zebra
28 | Pithampura | Rajgarh-PG | 2 | MPPTCL | MPPTCL | WRTS-1 | 78 | Single Zebra
29 | Rajgarh-PG | Rajgarh-MP | 1 | MPPTCL | WRTS-2 | MPPTCL | 13 | Single Zebra
30 | Rajgarh-PG | Rajgarh-MP | 2 | MPPTCL | WRTS-2 | MPPTCL | 12 | Single Zebra
31 | Satna-MP | Satna-PG | 1 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
32 | Satna-MP | Satna-PG | 2 | MPPTCL | MPPTCL | WRTS-2 | 1 | Single Zebra
33 | Satna-PG | Maihar | 2 | MPPTCL | WRTS-2 | MPPTCL | 42 | Single Zebra
34 | Seoni-PG | Seoni-MP | 1 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
35 | Seoni-PG | Seoni-MP | 2 | MPPTCL | WRTS-1 | MPPTCL | 4 | Single Zebra
36 | Seoni-PG | Chindwara | 1 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
37 | Seoni-PG | Chindwara | 2 | MPPTCL | WRTS-1 | MPPTCL | 67 | Single Zebra
[6 empty] | Total | 2442
400/220 kV ICTs
S.No | Sub-station | Id | MVA | Voltage Ratio | Owner
1 | Birsingpur | 1 | 500 | 400/220 | MPPTCL
2 | Satpura | 1 | 500 | 400/220 | MPPTCL
3 | Astha | 1 | 315 | 400/220 | MPPTCL
4 | Astha | 2 | 315 | 400/220 | MPPTCL
5 | Bhopal | 1 | 315 | 400/220 | MPPTCL
6 | Bhopal | 2 | 315 | 400/220 | MPPTCL
7 | Bhopal | 3 | 315 | 400/220 | MPPTCL
8 | Bina | 1 | 315 | 400/220 | MPPTCL
9 | Bina | 2 | 315 | 400/220 | MPPTCL
10 | Bina | 3 | 315 | 400/220 | MPPTCL
11 | Chegaon | 1 | 315 | 400/220 | MPPTCL
12 | Indore | 1 | 315 | 400/220 | MPPTCL
13 | Indore | 2 | 315 | 400/220 | MPPTCL
14 | Indore | 3 | 315 | 400/220 | MPPTCL
15 | Indore | 4 | 315 | 400/220 | MPPTCL
16 | Katni | 1 | 315 | 400/220 | MPPTCL
17 | Malwa | 1 | 315 | 400/220 | MPPTCL
18 | Nagda | 1 | 315 | 400/220 | MPPTCL
19 | Nagda | 2 | 315 | 400/220 | MPPTCL
20 | Nagda | 3 | 315 | 400/220 | MPPTCL
21 | Pithampur | 1 | 315 | 400/220 | MPPTCL
22 | Pithampur | 2 | 315 | 400/220 | MPPTCL
|  | Total | 7300
BRs at 400kV Substations
S.No | Name of S/S | Owner | Nos of Reactor | Total MVAR | Rated Voltage
1 | Bhopal | MPPTCL | 1X125 | 125 | 420
2 | Bina(MP) | MPPTCL | 1X50 | 50 | 420
3 | Birsinghpur | MPPTCL | 1X50 | 50 | 420
4 | Nagda | MPPTCL | 2X50 | 100 | 420
5 | Nagda | MPPTCL | 2X50 | 100 | 420
6 | Satpura | MPPTCL | 2X63 | 126 | 420
|  |  | Total | 551
LRs at 400kV Substations
Sr. No. | Name of the Line | Reactor capacity in MVAR
|  | End 1 |  | End 2
1 | Satpura-Seoni-S/C | - |  | 50
2 | Bhopal-Bina-1 | - |  | 50
3 | Bhopal-Bina-2 | - |  | 50
4 | Indore-Indirasagar-2 | 50 |  | -
5 | Damoh-Birsighpur-S/C | 50 |  | -
6 | Indore-Itarasi-1 | 50 |  | -
7 | Indore-Itarasi-2 | 50 |  | -
8 | Indore-Asoj-1 | 50 |  | -
9 | Nagda-Rajgarh-1 | 50 |  | -
10 | Nagda-Rajgarh-2 | 50 |  | -
11 | Nagda-Bina-1 | 63 |  | -
12 | Nagda-Bina-2 | 63 |  | -
13 | Nagda-Dehgam-1 | 50 |  | -
14 | Nagda-Dehgam-2 | 50 |  | -
| TOTAL | 576 |  | 150

## 315MVA ICTs
Sl No | Sub-station | Id | MVA | Voltage Ratio | Owner
1 | Akola | 1 | 315 | 400/220 | MSETCL
2 | Akola | 2 | 315 | 400/220 | MSETCL
3 | Amreli | 1 | 315 | 400/220 | GETCO | G
4 | Amreli | 2 | 315 | 400/220 | GETCO | G
5 | Amreli | 3 | 315 | 400/220 | GETCO | G
6 | Astha | 1 | 315 | 400/220 | MPPTCL
7 | Astha | 2 | 315 | 400/220 | MPPTCL
8 | Asoj | 3 | 315 | 400/220 | GETCO | G
9 | Aurangabad | 1 | 315 | 400/220 | MSETCL
10 | Aurangabad | 2 | 315 | 400/220 | MSETCL
11 | Aurangabad-PG | 1 | 315 | 400/220 | WRTS-1
12 | Aurangabad-PG | 2 | 315 | 400/220 | WRTS-1
13 | Bableshwar | 1 | 315 | 400/220 | MSETCL
14 | Bableshwar | 2 | 315 | 400/220 | MSETCL
15 | Bachau | 1 | 315 | 400/220 | WRTS-2 | G
16 | Bachau | 2 | 315 | 400/220 | WRTS-2 | G
17 | Balco | 1 | 315 | 400/220 | BALCO
18 | Balco | 2 | 315 | 400/220 | BALCO
19 | Balco | 3 | 315 | 400/220 | BALCO
20 | Betul | 1 | 315 | 400/220 | WRTS-2
21 | Betul | 2 | 315 | 400/220 | WRTS-2
22 | Bhadrawathi | 1 | 315 | 400/220 | WRTS-1
23 | Bhatapara | 1 | 315 | 400/220 | WRTS-1
24 | Bhatapara | 2 | 315 | 400/220 | WRTS-1
25 | Bhilai | 1 | 315 | 400/220 | WRTS-1
26 | Bhilai | 2 | 315 | 400/220 | WRTS-1
27 | Bhilai | 3 | 315 | 400/220 | WRTS-1
28 | Bhopal | 1 | 315 | 400/220 | MPPTCL
29 | Bhopal | 2 | 315 | 400/220 | MPPTCL
30 | Bhopal | 3 | 315 | 400/220 | MPPTCL
31 | Bhusawal | 1 | 315 | 400/220 | MSETCL
32 | Bina | 1 | 315 | 400/220 | MPPTCL
33 | Bina | 2 | 315 | 400/220 | MPPTCL
34 | Bina | 3 | 315 | 400/220 | MPPTCL
35 | Bina-PG | 1 | 315 | 400/220 | WRTS-2
36 | Boisar-PG | 1 | 315 | 400/220 | WRTS-2
37 | Boisar-PG | 2 | 315 | 400/220 | WRTS-2
38 | Carnac | 1 | 315 | 220/100 | MSETCL
39 | Carn-GIS | 1 | 315 | 220/100 | MSETCL
40 | Chakan | 1 | 315 | 400/220 | MSETCL
41 | Chakan | 2 | 315 | 400/220 | MSETCL
42 | Chandrapur | 1 | 315 | 400/220 | MSETCL
43 | Chandrapur | 2 | 315 | 400/220 | MSETCL
44 | Chegaon | 1 | 315 | 400/220 | MPPTCL
45 | Damoh | 1 | 315 | 400/220 | WRTS-2
46 | Damoh | 2 | 315 | 400/220 | WRTS-2
47 | Dehgam | 1 | 315 | 400/220 | WRTS-2 | G
48 | Dehgam | 2 | 315 | 400/220 | WRTS-2 | G
49 | Dhule | 1 | 315 | 400/220 | MSETCL
50 | Dhule | 2 | 315 | 400/220 | MSETCL
51 | Gwalior | 1 | 315 | 400/220 | WRTS-2
52 | Gwalior | 2 | 315 | 400/220 | WRTS-2
53 | Gwalior | 3 | 315 | 400/220 | WRTS-2
54 | Hadala | 1 | 315 | 400/220 | GETCO | G
55 | Hadala | 2 | 315 | 400/220 | GETCO | G
56 | Hadala | 3 | 315 | 400/220 | GETCO | G
57 | Indore | 1 | 315 | 400/220 | MPPTCL
58 | Indore | 2 | 315 | 400/220 | MPPTCL
59 | Indore | 3 | 315 | 400/220 | MPPTCL
60 | Indore | 4 | 315 | 400/220 | MPPTCL
61 | Itarsi | 1 | 315 | 400/220 | WRTS-2
62 | Jabalpur | 1 | 315 | 400/220 | WRTS-2
63 | Jabalpur | 2 | 315 | 400/220 | WRTS-2
64 | Jetpur | 1 | 315 | 400/220 | GETCO | G
65 | Jetpur | 2 | 315 | 400/220 | GETCO | G
66 | Jetpur | 3 | 315 | 400/220 | GETCO | G
67 | Jindal | 1 | 315 | 400/220 | JPL
68 | Jindal | 2 | 315 | 400/220 | JPL
69 | Kala | 1 | 315 | 400/220 | WRTS(II)
70 | Kala | 2 | 315 | 400/220 | WRTS(II)
71 | Karad | 1 | 315 | 400/220 | MSETCL
72 | Karad | 2 | 315 | 400/220 | MSETCL
73 | Karad | 3 | 315 | 400/220 | MSETCL
74 | Kasor | 1 | 315 | 400/220 | GETCO | G
75 | Kasor | 2 | 315 | 400/220 | GETCO | G
76 | Katni | 1 | 315 | 400/220 | MPPTCL | G
77 | Khandwa | 1 | 315 | 400/220 | WRTS-2
78 | Khandwa | 2 | 315 | 400/220 | WRTS-2
79 | Kharghar | 1 | 315 | 400/220 | MSETCL
80 | Kharghar | 2 | 315 | 400/220 | MSETCL
81 | Kolhapur | 1 | 315 | 400/220 | MSETCL
82 | Kolhapur | 2 | 315 | 400/220 | MSETCL
83 | Koradi | 1 | 315 | 400/220 | MSETCL
84 | Koradi | 2 | 315 | 400/220 | MSETCL
85 | Kosamba | 1 | 315 | 400/220 | GETCO | G
86 | Kosamba | 2 | 315 | 400/220 | GETCO | G
87 | Lonikhand | 1 | 315 | 400/220 | MSETCL
88 | Lonikhand | 2 | 315 | 400/220 | MSETCL
89 | Lonikhand | 3 | 315 | 400/220 | MSETCL
90 | Magarwada | 1 | 315 | 400/220 | WRTS-1 | G
91 | Magarwada | 2 | 315 | 400/220 | WRTS-1 | G
92 | Malwa | 1 | 315 | 400/220 | MPPTCL
93 | Mansar | 1 | 315 | 400/220 | GETCO | G
94 | Mansar | 2 | 315 | 400/220 | GETCO | G
95 | Mapusa | 1 | 315 | 400/220 | WRTS-1
96 | Mapusa | 2 | 315 | 400/220 | WRTS-1
97 | Mapusa | 3 | 315 | 400/220 | WRTS-1
98 | Marwa | 1 | 315 | 400/220 | CSPTCL
99 | Mundra | 1 | 315 | 400/220 | APL | G
100 | Mundra | 2 | 315 | 400/220 | APL | G
101 | Nagda | 1 | 315 | 400/220 | MPPTCL
102 | Nagda | 2 | 315 | 400/220 | MPPTCL
103 | Nagda | 3 | 315 | 400/220 | MPPTCL
104 | Nagothane | 1 | 315 | 400/220 | MSETCL
105 | Nagothane | 2 | 315 | 400/220 | MSETCL
106 | Navsari | 1 | 315 | 400/220 | WRTS-2 | G
107 | Navsari | 2 | 315 | 400/220 | WRTS-2 | G
108 | New Koyna | 1 | 315 | 400/220 | MSETCL
109 | NSPCL | 1 | 315 | 400/220 | NSPCL
110 | NSPCL | 2 | 315 | 400/220 | NSPCL
111 | Padghe | 1 | 315 | 400/220 | WRTS-2
112 | Padghe | 2 | 315 | 400/220 | WRTS-2
113 | Padghe | 3 | 315 | 400/220 | WRTS-2
114 | Parli | 1 | 315 | 400/220 | WRTS-1
115 | Parli | 2 | 315 | 400/220 | WRTS-1
116 | Pirana(T) | 1 | 315 | 400/132 | TPL | G
117 | Pirana(T) | 2 | 315 | 400/132 | TPL | G
118 | Pirana-PG | 1 | 315 | 400/220 | WRTS-2 | G
119 | Pirana-PG | 2 | 315 | 400/220 | WRTS-2 | G
120 | Pithampur | 1 | 315 | 400/220 | MPPTCL
121 | Pithampur | 2 | 315 | 400/220 | MPPTCL
122 | Pune-PG | 1 | 315 | 400/220 | WRTS-1
123 | Pune-PG | 2 | 315 | 400/220 | WRTS-1
124 | Pune-PG | 3 | 315 | 400/220 | WRTS-1
125 | Raigarh | 1 | 315 | 400/220 | WRTS-2
126 | Raigarh | 2 | 315 | 400/220 | WRTS-2
127 | Raipur | 1 | 315 | 400/220 | WRTS-1
128 | Raipur | 2 | 315 | 400/220 | WRTS-1
129 | Raipur | 3 | 315 | 400/220 | WRTS-1
130 | Raita | 1 | 315 | 400/220 | CSPTCL
131 | Raita | 2 | 315 | 400/220 | CSPTCL
132 | Rajgarh | 1 | 315 | 400/220 | WRTS-2
133 | Rajgarh | 2 | 315 | 400/220 | WRTS-2
134 | Ranchodpura | 1 | 315 | 400/220 | GETCO | G
135 | Ranchodpura | 2 | 315 | 400/220 | GETCO | G
136 | Ranchodpura | 3 | 315 | 400/220 | GETCO | G
137 | Satna-PG | 1 | 315 | 400/220 | WRTS-2
138 | Satna-PG | 2 | 315 | 400/220 | WRTS-2
139 | Seoni | 1 | 315 | 400/220 | WRTS-1
140 | Seoni | 2 | 315 | 400/220 | WRTS-1
141 | Sholapur-PG | 1 | 315 | 400/220 | WRTS-1
142 | Sholapur-PG | 2 | 315 | 400/220 | WRTS-1
143 | Shujalpur | 1 | 315 | 400/220 | WRTS-2
144 | Shujalpur | 2 | 315 | 400/220 | WRTS-2
145 | SSP | 1 | 315 | 400/220 | SSNL | G
146 | SSP | 2 | 315 | 400/220 | SSNL | G
147 | Sugen | 1 | 315 | 400/220 | TPL | G
148 | Sugen | 2 | 315 | 400/220 | TPL | G
149 | Sugen | 3 | 315 | 400/220 | TPL | G
150 | Ukai | 1 | 315 | 400/220 | GETCO | G
151 | Vapi | 1 | 315 | 400/220 | WRTS-2 | G
152 | Vapi | 2 | 315 | 400/220 | WRTS-2 | G
153 | Vapi | 3 | 315 | 400/220 | WRTS-2 | G
154 | Versana | 1 | 315 | 400/220 | GETCO | G
155 | Versana | 2 | 315 | 400/220 | GETCO | G
156 | Wanakbori | 1 | 315 | 400/220 | GETCO | G
157 | Wardha | 1 | 315 | 400/220 | WRTS-1
158 | Wardha | 2 | 315 | 400/220 | WRTS-1
159 | Zerda | 1 | 315 | 400/220 | GETCO | G
160 | Zerda | 2 | 315 | 400/220 | GETCO | G
161 | Zerda | 3 | 315 | 400/220 | GETCO | G
|  | Sub-Total | 50715

## FSC
Fixed Series Compensators (FSC)
S.N | Line Details | kV | Len (km) | FSC Location( %) | Compensation | Agency |  | Comments
1 | Seoni-Khandwa-1 | 400 | 350 | Khandwa | 40% | WRTS-2
2 | Seoni-Khandwa-2 | 400 | 350 | Khandwa | 40% | WRTS-2
3 | Rajgarh-Kasor-1 | 400 | 232 | Rajgarh | 25% | WRTS-2
4 | Rajgarh-Kasor-2 | 400 | 232 | Rajgarh | 25% | WRTS-2
5 | Raigarh-Raipur-3 | 400 | 220 | Raipur | 40% | WRTS-1
6 | Raigarh-Raipur-4 | 400 | 220 | Raipur | 40% | WRTS-2
7 | Adani-Sami-1 | 400 | 434 | Sami | 40% | APL
8 | Adani-Sami-2 | 400 | 434 | Sami | 40% | APL
9 | Raipur-Wardha-1 | 400 | 371 | Wardha | 40% | WRTS-1
10 | Raipur-Wardha-2 | 400 | 371 | Wardha | 40% | WRTS-1
B. Thyristor Controlled Series Capacitor (TCSC)
S.N | Line Detail | kV | Len ( km) | Location | Fixed, Variable |  | Agency
1 | Raipur-Raigarh-I | 400 | 217 | Raipur | 40% Fix, +15% / -5% Dynamic |  | WRTS-1
2 | Raipur-Raigarh-II | 400 | 217 | Raipur | 40% Fix, +15% / -5% Dynamic |  | WRTS-1 |  | Out of service since 11.04.2015